## Amendment - 1
NIT No: SECI/C&P/PMC/11/0001/2021-22
Tender for Design, Engineering, Supply, Construction, Erection, Testing, Commissioning and O&M of 5 MW (AC) Grid connected ground based SPV Project at V.O.Chidambaranar Port Trust (VOCPT), Tuticorin, Tamilnadu, India
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | Section - VII B. Technical Specifications | 68 of 112 | 21.5 | Overhead Transmission Line In case the power evacuation is planned with overhead transmission line for plant external evacuation, the design of tower and its accessories shall be as per the DISCOM / STU’s requirement and the design shall be submitted to Employer for approval/ accord. | Overhead Transmission Line In case the power evacuation is planned with overhead transmission line for plant external evacuation, the design of tower/pole and its accessories shall be as per the DISCOM / STU’s requirement and the design shall be submitted to Employer for approval/ accord.
2 | Section - VII B. Technical Specifications | 89 of 112 | 13.35 | The length of one unit (Table) of MMS shall generally not be more than 20m. | The length of one unit (table) of MMS shall generally not be more than 30m. Effects of temperature variation shall be duly considered in the MMS design.
3 | Section - VII B. Technical Specifications | 91 of 112 | 16.1.2 | Inverter, Switchgear panel, Metering panel and associated equipment shall be installed on plinth as open installations. The plinth supporting the ICR/LCR equipment shall have RCC framed structure with foundations, columns and beams built up to the plinth level (FFL). Plinth filling shall be provided as per the specifications for the same stipulated by the Clause No. 21 in Section VII-B of the tender document. Flooring shall be provided using 40 mm thick Cement concrete (IPS) flooring (1:2:4), aggregate size 10 mm down, conforming to IS 2571 with 2mm thick Heavy duty epoxy coating (Industrial grade) of approved make on top as per manufacturer specifications. There shall be suitable provision for easy passage of O&M personnel, cable trench, operating area, etc. as required. Weather canopy shall be provided for all open installations. Canopy columns shall be supported on pedestals at plinth level. | Outdoor equipment (Inverter, Switchgear panel, Metering panel, etc.) shall be installed on plinth as open installations. The plinth supporting the equipment shall have RCC framed structure with foundations, columns and beams built up to the plinth level (FFL). Plinth filling shall be provided as per the specifications for the same stipulated by the Clause No. 21 in Section VII-B of the tender document. Flooring shall be provided using 40 mm thick Cement concrete (IPS) flooring (1:2:4), aggregate size 10 mm down, conforming to IS 2571 with 2mm thick Heavy duty epoxy coating (Industrial grade) of approved make on top as per manufacturer specifications. There shall be suitable provision for easy passage of O&M personnel, cable trench, operating area, etc. as required. Weather canopy shall be provided for all open installations. Canopy columns shall be supported on pedestals at plinth level. If indoor equipment are provided, they shall be installed inside MCR/any other PEB placed on plinth having RCC framed structure with foundations, columns and beams built up to the plinth level (FFL).
4 | Annexure - G Operation & Maintenance Agreement | 38 of 45 | 1(C) | … Eac is the number of units recorded in the plant end ABT meter excluding auxiliary consumption, kWh … | … Eac is (Number of units recorded in the substation end ABT meter) - (Plant Auxiliary consumption), kWh …
5 | Section -VII | - | - | Tender No.: SECI/C&P/NIT/2021/VOCPT5 | Tender No.: SECI/C&P/PMC/11/0001/2021-22
6 | Annexure to BDS Qualifying Requirements | 3 of 7 | 1.3 | The Minimum Average Annual Turnover (MAAT) of the bidder in the last three financial years (i.e. FY 2016-2017, 2017-18 and 2018-19) should be INR 10,04,00,000/- (Indian Rupees ten crores & four lakhs only). MAAT shall mean Revenue from Operations as incorporated in the profit & loss account excluding other income, e.g. sale of fixed assets. This must be the individual Company’s turnover and not that of any group of Companies. A summarized sheet of average turnover, certified by a practicing Chartered Accountant/Statutory Auditor should be compulsorily enclosed along with corresponding annual accounts. | The Minimum Average Annual Turnover (MAAT) of the bidder in the last three financial years (i.e. FY 2018-2019, 2019-20 and 2020-21) should be INR 10,04,00,000/- (Indian Rupees ten crores & four lakhs only). MAAT shall mean Revenue from Operations as incorporated in the profit & loss account excluding other income, e.g. sale of fixed assets. This must be the individual Company’s turnover and not that of any group of Companies. A summarized sheet of average turnover, certified by a practicing Chartered Accountant/Statutory Auditor should be compulsorily enclosed along with corresponding annual accounts.
7 | Section-I Invitation for Bids | 8 of 10 | (I)
8 | Section-III BDS | 3 of 5 | 7 | “Not Applicable”. Only Bid Securing Declaration is to be submitted in line with the form as attached under Section VI, “Sample forms & formats” | “Applicable”. EMD is to be submitted in line with the form as attached under Section VI, Form F-4A.
9 | Section-VI Sample Forms and Formats | - | New Form is attached | - | Form 12 'DECLARATION REGARDING THE PROCUREMENT OF SOLAR INVERTERS & SOLAR MODULES FROM CLASS I LOCAL SUPPLIERS' is attached.
10 | Section-V Special Conditions of Contract | 6 of 11 | 13 | Add following to the existing clause: 1. During the Operational Acceptance after providing 03 chances for the PR demonstration, any shortfall in the Performance Ratio (PR) as determined through the PR Test Procedure specified in Section VII, Scope of Work and Technical Specifications, & “PERFORMANCE GUARANTEE TEST PROCEDURE”, will attract imposition of penalty. For every 1% shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Sup ........................................... ...............case if there is a component/Machine/Inverter failure. SECI shall bear the deviation charges on account of such failure till the time period block before which the revision of scheduling is not allowed, affected as per applicable regulation. The contractor shall bear the deviation charges due to such failure beyond such time period. | Void
11 | Section-II Instruction to Bidders | 13 of 47 | 13.4 (b) | The base date for the purpose of applying statutory variation shall be the last date of bid submission. | The base date for the purpose of applying statutory variation shall be the date after the date seven (7) days prior to the date of Bid submission, in the country where the Site is located
12 | Section - VII B. Technical Specifications | 25 of 112 | 5.6.1 | Type Tests and Special Tests The following type test and special test reports shall be submitted during detailed engineering. The tests should have been conducted on the similar transformer by NABL accredited laboratory. | Type Tests and Special Tests The following type test and special test reports shall be submitted during detailed engineering. The tests should have been conducted on the similar transformer by NABL accredited laboratory within last five years from the last date of bid submission.
13 | Section-V Special Conditions of Contract | 11 of 11 | Add New Clause No 21 in SCC for GCC Clause 19.4 | Upon occurrence of such causes, the party alleging that it has been rendered unable as aforesaid, thereby, shall notify the other party in writing by registered notice within 48 (forty eight) hours of the alleged beginning thereof giving full particulars and satisfactory evidence in support of its claim. Further, within 7 (seven) days, the Contractor will furnish a detailed Contingency Plan to overcome the effects of the incident and bring the project on its schedule after cessation of the effect of Force Majeure. | Replace the existing clause by following: Upon occurrence of such causes, the party alleging that it has been rendered unable as aforesaid, thereby, shall notify the other party in writing by registered notice within 7 (Seven) days of the alleged beginning thereof giving full particulars and satisfactory evidence in support of its claim. Further, within 14 (Fourteen) days, the Contractor will furnish a detailed Contingency Plan to overcome the effects of the incident and bring the project on its schedule after cessation of the effect of Force Majeure.

## Pre Bid Queries Clarifications
Tender for Design, Engineering, Supply, Construction, Erection, Testing, Commissioning and O&M of 5 MW (AC) Grid connected ground based SPV Project at V.O. Chidambaranar Port Trust (VOCPT), Tuticorin, Tamilnadu, India
NIT No: SECI/C&P/PMC/11/0001/2021-22
S. No. | Tender Section | Page No | Clause No | Description as per Tender Document | Queries | Category (Technical/Contractual/Financial) | Clarifications
1 | ITB | 13 of 47 | 13.4 | The base date for the purpose of applying statutory variation shall be the last date of bid submission. | As per cl no. 51.1 of GCC the base date to be considered as " after the date seven (7) days prior to the date of Bid submission, in the country " .Kindly confirm which clause to the referred | Contractual | Kindly refer Amendment 1 for the same.
2 | GCC | 44 of 78 | 51.1 | However, these adjustments would be restricted to direct transactions between the Owner and the Contractor. This adjustment shall not be applicable on procurement of raw materials, intermediary components etc. by the Contractor and shall also not be applicable on bought out items dispatched directly from sub- vendor works to site. | In case of imposition of any new laws on the custom duty or any change in the rates of custom duty should be treated under as 'Change in Tax ' or 'Imposition of new laws' and and necessary adjustments should be given as these variations have direct impact on the Project Cost .Also any supply transaction , direct and indirect , should come under the 'change in taxation' clause | Contractual | The terms and conditions of the tender document shall prevail.
3 | GCC | 54 of 78 | 73.15 | Notwithstanding anything contrary contained herein, the aggregate total liability of Contractor under the Agreement or otherwise shall be limited to 100% of Agreement/ Contract Value except in case of Patent Infringement liability. However, neither party shall be liable to the other party for any indirect and consequential damages, loss of profits or loss of production | Kindly consider the total Liability of the Contract up to 10% of the Contract Value | Contractual | The terms and conditions of the tender document shall prevail.
4 | SCC | 5 of 11 | 11 | Contract Performance Security submitted shall be released to the Contractor without any interest not later than 75 (Seventy- Five) days after the successful completion of the complete O&M period (10 Years) subject to the approval and acceptance of the O&M period deliverables. | We understand that the PBG needs to have validity of 132 months but can be released after 75 days from 129 months on completion of 10 years of O&M period | Contractual | The PBG clause is self explanatory for the validity period & further for its release.
5 | SCC | 6 of 11 | 13 | Liquidated damages during O&M period against breakdown of other Infrastructure of Plant which doesn’t affect the generation of power, directly such as but not limited to civil infrastructure, water supply system/network, other Infrastructure developed by the Contractor as a Scope of Work for the Project (Section-VII: Scope of Works & Technical Specifications) shall be penalized @ Rs.1000/day, per incident of breakdown reported beyond 07 Days of such reporting. Cumulative value of such penalty shall be limited to 50% of yearly O&M cost. | Completion time of rectification entirely depend on the quantum and the nature of the fault . Hence we request to impose penalty if the rectification work has not started within 7 days of reporting of any fault . Also as there will be penalty due to shortfall in achieving CUF , this is a duplication of penalty and hence this clause should be deleted | Contractual | The terms and conditions of the tender document shall prevail.
6 | SCC | 7 of 11 | 16 | Interest bearing adjustable initial advance (OPTIONAL) of 10% of the Contract Value (i.e., total sum of all the Supply Contract) shall be released to successful bidder upon receipt of unconditional acceptance of NOA, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final commissioning total amounting to 110% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security. The annual interest rate shall be calculated based SBI one-year MCLR as applicable. | Request to allow interest free mobilization advance against submission of equivalent amount of Advance Bank Guarantee | Contractual | The terms and conditions of the tender document shall prevail.
7 | Technical Spec | 6 of 17 | 4 | Adequate capacity of Solar PV Modules with minimum DC capacity as mentioned in Clause 1 of Scope of Works. Module Mounting Structure (MMS) with necessary hardware suitable for mounting PV Modules. | Please confirm if only fixed type MMS to be used | Technical | Only fixed tilt MMS is allowed. Kindly refer Clause 1 of Scope of Works. The terms and conditions of the tender document shall prevail.
8 |  |  |  |  | Please confirm if only Indian Modules with Indian Cells are to be used | Technical | Kindly refer Clause 1.3.2 of 'Technical Specifications - Electrical System'. The PV Module Supplier shall be Class-I local supplier as per MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of Renewable Energy (RE) Sector dated 9th February, 2021 and subsequent amendments. The terms and conditions of the tender document shall prevail.
9 | Annexure-C | 3 of 10 | 2.1 | A Performance Ratio Guarantee test shall be commenced within 60 days of the commissioning of Plant Facilities to demonstrate that the plant has achieved the Guaranteed Performance Ratio in line with requirements under section VII of the bidding document | By commissioning we mean synchronization of the entire system to the 22 KV substation .Please confirm | Technical | Kindly refer Clause 1.1.22 of GCC for definition of Commissioning. The terms and conditions of the tender document shall prevail.
10 | BDS | 3 of 5 | 7 | “Not Applicable”. Only Bid Securing Declaration is to be submitted in line with the form as attached under Section VI, “Sample forms & formats” | As per cl no IFB I-Amount: INR 50,00,000 (Indian Rupees Fifty Lakhs only). Please confirm EMD is applicable or not. If EMD applicable, please share the details for preparing the Bank Guarantee - Name of Bank ,Branch name,IFSC code & EMD format If not Please share the Bid securing Declaration form | Contractual | EMD of INR 50,00,000 (Indian Rupees Fifty Lakhs only) is applicable as mentioned in tender document. The typographical errors regarding the EMD have been corrected in the Amendment 1. Please refer to Form F-4A for the EMD format in the tender document.
11 | Technical Spec | 10 of 17 | 5.13 | Installation, Testing and Commissioning of 22 kV Over Head Transmission Line / Underground Cable from Plant take-off point to Interconnecting Substation including laying of underground cable at railway siding of SPIC chemical factory through 250 mm diameter GI pipe (top of pipe at minimum 1.0 m below rail sleeper) through horizontal directional drilling method. The cable shall be laid strictly as per the approving authority. The work should not disturb the operations of the railway line. | Please confirm for Railway crossing permission need to be taken from whom - Factory owner or Railway Department. Also please share working in the Coastal Area is any special type of permission is required | Technical | Railway crossing permission needs to be taken from Railways Department. The Contractor shall acquire CRZ clearance on behalf of owner. VOCPT will facilitate. The terms and conditions of the tender document shall prevail.
12 | Technical Spec | 12 of 17 | 7.1 | Obtaining statutory approvals /clearances on behalf of the Employer from various Government Departments, not limited to, the following: | As the land is inside the premises of the Port Area hence all the statutory approvals except CEIG/CEA , DISCOM should be under VOCPT'S scope | Technical | The Contractor shall acquire all necessary statutory approvals/permissions on behalf of owner. VOCPT will facilitate. The terms and conditions of the tender document shall prevail.
13 | Inverter Transformer and Auxiliary Transformer | 261 | 5.2 | Inverter Transformer VA Rating 2 x 2.5 MVA | Please allow us to install Inverter duty transformer of 5 MVA capacity. | Technical | The terms and conditions of the tender document shall prevail.
14 | Lightning Protection System | 289 | 13.2 | Lightning Protection Level for the entire plant shall be Level-III. | For the Solar power plant design, protection level shall be level-IV. Please accept. | Technical | The terms and conditions of the tender document shall prevail.
15 | Power Evacuation System | 308 | 21.5 | In case the power evacuation is planned with overhead transmission line for plant external evacuation, the design of tower and its accessories shall be as per the DISCOM / STU’s requirement and the design shall be submitted to Employer for approval/ accord. | As we have to evacuate 5MW power in 22kV line, hence we mayn't require any tower for transmission. Transmission line using pole is enough. Kindly clarify. | Technical | Kindly refer S.No.1 of Amendment-1.
16 |  |  |  |  | Can we go with conventional system instead of CSS. | Technical | CSS is not specified in the tender. Kindly refer 'Technical Specifications-Electrical System' for details.
17 |  |  |  |  | Which system to be considered? Earthed or Un earthed system? | Technical | Inverter transformer neutral earthing shall be as per the requirements of inverter manufacturer.
18 |  | 277 | 7.5 | For HT cables (from inverter transformer to interconnection point), maximum voltage drop shall be limited to 0.5 % of the rated voltage. | Here we understood that the maximum voltage drop shall be limited to 0.5 % of the rated voltage from inverter transformer to plant end ABT metering point. | Technical | 'Description as per Tender Document' of the clause referred here by the bidder is different from that mentioned in the tender document. For the sake of clarity, part of Clause 7.5(ii) of 'Technical Specifications-Electrical System' pertinent to the query is reproduced below. "...For HT cables (from inverter transformer to plant take off point), maximum voltage drop shall be limited to 0.5 % of the rated voltage...." The terms and conditions of the tender document shall prevail.
19 |  |  |  | MCR | In tender different types of specifications are given in the the the tender. Request you to confirm the same | Technical | Kindly refer Clause 16.1.3 of 'Technical Specifications - Civil, Mechanical and Plumbing Works' where it is clearly specified that MCR shall be a pre-engineered building.
20 | Module Mounting Structure (MMS) | 329 | 13.35 | The length of single table shall not be more than 20m. | The Length of one MMS Unit should be according to String Size. Please Clarify For 1500V system, table length will be 30m for 2PX30 table size. Please allow the same. | Technical | Kindly refer S.No.2 of Amendment-1.
21 | VII - B | 316 | 5.4 | Mandatory permissions/ licenses/ statutory clearances from competent authorities if required for cutting of trees, blasting or mining operations, disposal of waste material etc. shall be obtained by the contractor. | Cutting of big trees & removal & uprooting shall be in client scope. Removal of shrubs, bushes, vegetation, small plants shall be in bidder scope. | Technical | Cutting of big trees & removal & uprooting, Removal of shrubs, bushes, vegetation, small plants shall be in bidder scope. The terms and conditions of the tender document shall prevail.
22 | PV Module Cleaning System – Wet or Dry Type | 345 | 35.4 | As the ground water contains high concentration of chlorides, it is not suitable for construction and module cleaning purposes. Suitable water for construction and module cleaning purposes (during plant operation) including its storage shall be arranged by the Contractor. | Source of water for construction & module cleaning shall be identified by client. Supply & other facilities shall be in bidder scope. | Technical | Suitable water for construction and module cleaning purposes (during plant operation) including its storage shall be arranged by the bidder. The terms and conditions of the tender document shall prevail.
23 |  | 346 |  | Water storage tank shall be of Overhead water type. | Instead of overhead RCC water tank, on ground PVC / Syntex / similar arrangements will be provided. | Technical | Description as per Tender Document' mentioned here by the bidder is different from that mentioned in the tender document on the referred page number. As per clause 36.1 of 'Technical Specifications-Civil, Mechanical and Plumbing Works', Water storage tank (wherever required) of required capacity shall be of overhead/over ground type and made of RCC or PVC as per design requirements. The terms and conditions of the tender document shall prevail.
24 |  | 248 |  | IEC 62804-1:2015 Ed.1 : Test methods for the detection of potential-induced degradation - Part 1: Crystalline silicon (under conditions of 85oC/85% RH for minimum 192 hours) | VSL modules are tested as per standard IEC 62804 test procedure for 96hrs | Technical | The terms and conditions of the tender document shall prevail.
25 |  | 252 | 1.7.6 | Maximum three numbers of bins will be allowed for each module rating | VSL to provide 2 current bins in a given module power bin. | Technical | The number of bins shall be decided such that current mismatch of modules within a bin is below acceptable limit. The terms and conditions of the tender document shall prevail.
26 |  | 457 |  | Eac is the number of units recorded in the plant end ABT meter excluding auxiliary consumption, kWh | There are contradictory requirement in tender. Please confirm the ABT meter position (plant end or S/S end) for CUF and PR calculation. | Technical | Kindly refer S.No.4 of Amendment-1. Performance Ratio will be measured at the plant end ABT meter, whereas CUF will measured at the substation end ABT meter.
27 | PV Module Cleaning System – Wet or Dry Type | 346 | 35.11 | Module cleaning procedure and pressure requirement at discharge point shall be as per the recommendation of PV module manufacturer. However, discharge pressure at outlet shall not be less than 5 kgf/cm2 (0.5 MPa). | As per stand ard practice 4 to 6 Kg/cm2 (4-6 bar) pressure considered at outlet. Please confirm the pressure at cleaning point. | Technical | The terms and conditions of the tender document shall prevail.
28 | Module Mounting Structure (MMS) | 328 | 13.25 | Two numbers of anti-theft fasteners of stainless steel on two diagonally opposite corners for each module shall be provided. All fasteners and washers (2 round + 1 spring) both for MMS connections and fixing of PV Module shall be adequately protected from atmosphere and weather prevailing in the area. | Anti theft fasterners will obstruct the easy replacement of defected modules with new one. Please confirm. | Technical | The terms and conditions of the tender document shall prevail.
29 |  | 155 | 11 | The value of the Contract Performance Security shall be 4% (Four percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 132 Months (09 Months Project commissioning period) + 120 Months O & M Period + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of one year and the same may be extended every year till completion of the total 132 months period. | As per MOM of Ministry of Finance, Kindly accept the Contract Performance security 3% of the contract value | Contractual | Please refer MNRE Order No F. No. 283/114/2018-GRID SOLAR dated 16.12.2021, wherein the Performance Security is 4% only for the projects wherein the site is specified by the procurer.
30 | Project Particulars | 227 | 1 | Distance to interconnecting substation 4 km (approx.) | Please mention the type(Private/ Govt) of land falling under the transmission line | Technical | Solar plant location is with in VOCPT premises. The area from proposed Solar power plant location up to the boundary of VOCPT is belongs to VOCPT. The area beyond VOCPT boundary and up to substation is under Public/Private domain. Tentative route map of transmission line is attached for reference.
31 | Procurement and Supply | 230 | 4.27 | CCTV cameras with monitoring station along with mounting poles, power supply cables, communication cables, conduits, fittings, etc. The CCTV connectivity is to be linked with surveillance monitoring system of VOCPT Admin Building. All necessary communication cables, network switches and associated equipment for interconnection. | SECI to provide information regarding interfacing with existing VOCPT surveillance CCTV during DDE | Technical | Interface requirements will be provided during Detailed Engineering. The terms and conditions of the tender document shall prevail.
32 | Photovoltaic Modules | 250 | 1.4.2 | The Employer reserves the right to conduct Pressure Cooker (PC) test/ Highly Accelerated Stress Test (HAST) to confirm the durability of the back sheet in accelerated conditions. | PC test report from supplier can be provided but on shop test facility. Requested to exclude or Please consider the same | Technical | The terms and conditions of the tender document shall prevail.
33 | Solar and DC Cables | 254 | 3.5 (ii) | In case of central inverters, average voltage drop in the cables (from PV Modules to PCU) shall be limited to 1.5 % of the rated voltage. In case of string Inverters, average voltage drop (from PV module to string inverter) shall be limited to 0.5% of the rated voltage drop. The Contractor shall provide voltage drop calculations in excel sheet. | In case of central inverters, average voltage drop in the cables (from PV Modules to PCU) shall be limited to 2 % of the rated voltage. Please Consider | Technical | The terms and conditions of the tender document shall prevail.
34 | AC Cables | 277 | 7.5 (ii) | In case of Central inverters, maximum voltage drop in LT cable (from PCU to inverter transformer) shall be limited to 0.5% of the rated voltage. In case of String inverters, maximum voltage drop (from string inverter to LT combiner panel and from LT combiner panel to Inverter duty transformer) shall be limited to 1.5%. For HT cables (from inverter transformer to plant take off point), maximum voltage drop shall be limited to 0.5 % of the rated voltage. The Contactor shall provide voltage drop calculations in excel sheet. | 1) Here we understood that the maximum HT voltage drop shall be limited to 0.5 % of the rated voltage from inverter transformer to plant end ABT metering point. 2) If not, then request SECI to consider HT voltage drop from inverter transformer to plant take off point on actual Loss as 22V transmission include both Underground & Overhead Line. | Technical | Plant take off point shall mean the point on Solar plant boundary from where transmission line to interconnecting substation starts. The terms and conditions of the tender document shall prevail.
35 | illumination | 298 | 16.3.4 | Plant boundary/ Peripheral area shall be illuminated with chain-link/Boundary wall post mounted LED floodlights (at every 100m) for area lighting | 1. Street light is proposed instead of floodlights to reduce auxiliary power consumption. Please Consider 2. Please specify the wattage/Lux level of LED street light / flood light to be maintained in the periphery. | Technical | Specifications of LED flood light is provided in Clause 16.3.4 of 'Technical Specifications-Electrical System'. The terms and conditions of the tender document shall prevail.
36 |  | 467 |  | The Transmission Line consist of UG & OH Line for 4km (As per marking shown in Tender) | Kindly specify 1) Road Crossing Section - Min Height to maintain | Technical | Minimum height to be maintained for road crossing of overhead transmission line, if allowed, shall be as per IS codes / CEA regulations / DISCOM requirements.
37 |  | 468 |  | There is a Railway Crossing in the Transmission Line Path | Kindly Specify 1) The Width & Height of the Railway crossing. 2) Is the Railway Line driven by Electric Current or Diesel Engine. 3) Presence of any existing Cable Bridge or need to construct a new one. 4) Approvals required | Technical | 1) Details are not available. Kindly visit the site for these details. 2) Railway Line is driven by Electric Current. 3) Details are not available. Kindly visit the site for these details. 4) Permission needs to be taken from Railways Department.
38 | Procurement and Supply | 230 | 4.13 | The underground cable shall also pass under an existing railway siding of SPIC chemical factory with due approvals from concerned authorities. | This is contradictory to what is marked in kmz file. Railway crossing falls in OH Transmission line segment. Please Clarify | Technical | In page-3 of 'Annexure-H of Section-VII' (Transmission line route), underground cable is indicated by red color. Kindly refer page-4 of 'Annexure-H of Section-VII' (Railway crossing) where railway crossing is indicated in red color which means underground cable. The terms and conditions of the tender document shall prevail.
39 |  | 465 |  | 22kV Existing Substation | Kindly specify the following information 1) 22kV Feeder / Line Bay Availability 2) Fault Current Level | Technical | 1) 22 kV bay shall be constructed by the Contractor. 2) Data not available. Kindly visit the substation for details.
40 | C Civil, Mechanical and Plumbing Works | 329 | 13.34 | The Bidder should design the structure height considering highest flood level at the site and the finished grade level. The minimum clearance between the lower edge of the module and the finished grade shall be the higher of (i) Highest flood level + 100mm and (ii) 500 mm, as applicable | Please provide HFL (High Flood Level) of the Site | Technical | Highest High Water Level at Tuticorin w.r.t chart datum is +1.26m and the Mean Sea Level at Tuticorin w.r.t chart datum is +0.64m.
41 | C Civil, Mechanical and Plumbing Works | 312 313 | 3.3 | The field investigations shall mainly include drilling of min. 5 m deep BHs, The BH near MCR and ICR shall be 10m deep. | Foundation depth of structures shall be well within 5 m depth. So boreholes of 10 m depth will not be required. Please confirm the same. | Technical | The terms and conditions of the tender document shall prevail.
42 | C Civil, Mechanical and Plumbing Works | 312 313 | 3.3 | There shall be minimum 1 nos. of BH per 10 acres of the area. In case the project plot is divided in to number of discrete blocks separated from each other, min. 3 nos. of bore holes, 2 trial pits, 2 ERT and 2 CBR tests shall be taken per such block with at least 1 No. of BHs per 5 acres. | Provision of boreholes at each 10 acre will increase the timeline for soil investigation report. So it is proposed to consider one borehole per 12.5 acre of Land area. | Technical | The terms and conditions of the tender document shall prevail.
43 | C Civil, Mechanical and Plumbing Works | 316 | 5.4 | The contractor is responsible for making the site ready and easily approachable by clearing bushes, felling of trees (mandatory permissions/ licenses/ statutory clearances from competent authorities if required for cutting of trees, blasting or mining operations, disposal of waste material etc. shall be obtained by the contractor), | Cutting & removal of big trees (if any) and relevant permissions shall be in client scope. Removal of bushes, shrubs etc shall be in bidders scope. Please confirm the same. | Technical | Cutting of big trees & removal & uprooting , Removal of shrubs, bushes, vegetation, small plants shall be in bidder scope. The terms and conditions of the tender document shall prevail.
44 | C Civil, Mechanical and Plumbing Works | 316 | 5.4 | Except in exceptional cases (with approval of the Engineer), filling shall be made up of cohesive non-swelling material. | Backfilling shall be done with excavated soil with proper compaction. Please confirm the same. | Technical | The terms and conditions of the tender document shall prevail.
45 | 6 Roads | 318 | 6.1 | There shall be no peripheral road. However, about 2.5m wide corridor compacted to a depth of 300mm shall be left along inside of the plant boundary suitably maintained clean of any vegetation and shall be provided with adequate illumination for movement of security personnel. Any undulations shall be made good with locally available coarse grained material to have fairly level passage way. | Please allow 2.5m wide corridor roller compacted to a depth of 200mm. Please confirm the same. | Technical | The terms and conditions of the tender document shall prevail.
46 | 6 Roads | 318 | 6.8 | Minimum dia. of casing pipe to be used at any facility like electric cable, water pipe line etc. shall be 150mm. | 150 mm dia is not required for water pipe line please consider 50 mm & 32 MM dia for water pipe line i.e. standard practice | Technical | The terms and conditions of the tender document shall prevail.
47 | 7 Surface/ Area drainage | 320 | 7.15 | the Contractor shall explore provisions for rain water harvesting system for water conservation by constructing suitable collection wells along the drains or through provision of detention ponds or percolation/recharge pit etc. at major drainage outfalls. | In case there are no outfall point for discharging storm water, then only recharge pit will be provided. Please confirm the same. | Technical | A drainage system essentially has at least one outfall to discharge storm water outside the plant premises. The terms and conditions of the tender document shall prevail.
48 | 13 Module Mounting Structure (MMS) | 329 | 13.36 | The length of any cold formed section (CFS) shall not be more than 5.5 m. | For purlin, please allow length up to 6.0 m. | Technical | The terms and conditions of the tender document shall prevail.
49 | 8.3 Chain link fencing | 321 | 8.3.8 | Each fence panel, in lieu of tie wire, shall be provided with 35x35x3mm GI edge angle at top and bottom with mesh fabric firmly secured to them and to intermediate support angles | If the angle size mentioned in unavialble in the market, required size of MS flat will be provided. Please confirm the same. | Technical | The Contractor may propose higher section size in case of unavailability of mentioned size in the market. The terms and conditions of the tender document shall prevail.
50 | 10 Design Loads | 324 | 10.10.2 | For estimation of design wind loads on purlins (Table 8 of IS 875- Part 3), WL (downward) and WL (upward) on modules (laid in the profile of mono slope canopy) shall be applied such that the center of pressure should be at (0.3 × length of canopy) from windward end (for simplicity, the wind load distribution may be taken as triangular with max. value at windward end). Solidity ratio (∅) shall be taken as 0.0. | The triangular load consideration shall be applied only in exterior 2 tables along all periphery. For other interior tables, uniformly distributed load will be applied. Please confirm the same. | Technical | The terms and conditions of the tender document shall prevail.
51 | 36 PV Module Cleaning System | 346 | 36 | PV Module Cleaning System – Wet or Dry Type | It is proposed that Module Cleaning System will be provided as Wet Cleaning System with Water. Please confirm the same. | Technical | The referred clause allows both wet and dry cleaning system. The terms and conditions of the tender document shall prevail.
52 | 35 Wet type Cleaning System | 345 | 35.7 | The module cleaning system shall include construction of RCC tank or supply and installation of Ground mounted PVC tank (s) of required storage capacity, | Module Cleaning System water tanks will be Ground mounted PVC tanks of required storage capacity. Please consider the same. | Technical | The referred clause allows both RCC and PVC tank. The terms and conditions of the tender document shall prevail.
53 | 36 Overground Water Tank | 346 | 36.1 | Water Storage tank (wherever required) of required capacity shall be of overhead/over ground type and made of RCC or PVC as per design requirements. | It is suggested that Water Storage tank (wherever required) of required capacity shall be of over ground type and made of PVC as per design requirements. Please confirm the same. | Technical | The referred clause allows both RCC and PVC tank. The terms and conditions of the tender document shall prevail.
54 | C Civil, Mechanical and Plumbing Works | 317 | 6.2 | The approach road connecting nearest public road and the Main gate shall be of 4.0m wide carriage way with 0.5m wide shoulders on either side. | The approach road connecting nearest public road and the Main gate shall be of 3.5m wide carriage way with 0.5m wide shoulders on either side. | Technical | The terms and conditions of the tender document shall prevail.
55 | C Civil, Mechanical and Plumbing Works | 317 | 6.3 | 6.3 However, following minimum road section details shall be followed: (i) Topping: 75 mm thick PCC (1:2:4) (ii) Base course WBM : 125mm compacted thick, Grade III (iii) Base course WBM : 125 mm compacted thick, Grade II (iv) Granular/ gravel sub-base course = 350 mm compacted thick, compacted to 98% of max dry density (v) Compacted subgrade: 300mm thick below sub-base (non-expansive soil) in layers of 150mm thickness. (vi) Shoulders: 150mm compacted thick, murrum blended with WBM Grade-III | It is suggested that road will be as per following minimum section details : i) Base course WBM : 75mm compacted thick, Grade III (Mixed with binder course) ii) Base course WBM : 100 mm compacted thick, Grade II iii) Granular/ gravel sub-base course : 150 mm compacted thick. iv) Compacted sub grade: well compacted sub-grade 95% standard Procter MDD with no objectionable materials. v) Shoulders :150mm compacted thick, murrum blended with WBM Grade-III | Technical | The terms and conditions of the tender document shall prevail.
56 | C Civil, Mechanical and Plumbing Works | 320 | 8 Peripheral Chain Link Fence 8.2 | The fencing shall be with 2.5m height above grade level including 400mm dia. GI concertina wire along with 3 no. of barbed wires on either arm to be fixed on Y shape angle brackets. | The fencing shall be with 2.0m height above grade level including 400mm dia. GI concertina wire along with 2 no. of barbed wires on either arm to be fixed on Y shape angle brackets. | Technical | The terms and conditions of the tender document shall prevail.
57 | C Civil, Mechanical and Plumbing Works | 321 | 8.3.4 Chain link fencing | Spacing of intermediate posts shall not be more than 2.5m. | Spacing of intermediate posts shall not be more than 3m. Please confirm the same. | Technical | The terms and conditions of the tender document shall prevail.
58 | C Civil, Mechanical and Plumbing Works | 331 | 16 Buildings and Plinth for Open Installations | 16.1.4. The minimum plinth height (FFL) for all buildings and open installations shall be 1000 mm above FGL. | The minimum plinth height (FFL) for all buildings and open installations shall be 450 mm above FGL. Please confirm the same. | Technical | The terms and conditions of the tender document shall prevail.
59 | C Civil, Mechanical and Plumbing Works | 332 | 16 Buildings and Plinth for Open Installations | 16.1.6. Roof slab shall have projection of 450mm beyond external walls. | Roof slab shall have projection of 300mm beyond external walls. Please confirm the same. | Technical | The terms and conditions of the tender document shall prevail.
60 | C Civil, Mechanical and Plumbing Works | 343-344 | 34 Transformer Yard Civil Works | The area shall be provided with galvanized chain link fence of height min 1.8m with 3.5m wide gate. The specifications for fencing shall be similar to those specified under Cl. No. 31.3 except fence post which shall be of MS angle (ISA 65x65x6) spaced at 2.5 m c/c. | As per optimized solution point of view fence post which shall be of MS angle (ISA 50X50X6) spaced at 3 m c/c. Please confirm the same. | Technical | The terms and conditions of the tender document shall prevail.
61 | C Civil, Mechanical and Plumbing Works | 343-344 | 34 Transformer Yard Civil Works | 34.7 The Gate of size 3.5m shall be of MS pipe (medium class conforming to IS: 1161) frame with hard drawn steel wire fabric mesh (50x50mmx3mm thick conforming to IS: 1566) including all accessories and fittings. MS angle posts shall conform to IS 2062. 34.8 In addition to main gate a wicket gate of MS pipe (medium class conforming to IS: 1161) frame with 1.0 m width with hard drawn steel wire fabric (50x50x3mm thick conforming to IS: 1566) shall be provided for man entry for maintenance purpose. | No wicket gate is required in addition of main entry gate for transformer yard, please confirm the same. | Technical | The terms and conditions of the tender document shall prevail.
62 | REPORT ON SUB-SOIL INVESTIGATION | 476 | 8.1: PILE FOUNDATION: | The summary of Pile Carrying Capacity calculations are presented as follows. Necessary calculation sheets are presented in Calculation 1-5. Assume the depth of pile cap as 0.50 m from the existing ground level. | As per calculation Safe Pullout Capacity & Safe Compression Capacity are provided but Safe Lateral Load Capacity is not provided. Please provide Safe Lateral load Capacity of Pile, if available. | Technical | Not available.
63 | IFB | 11/533 | I | EARNEST MONEY DEPOSIT (EMD) | Kindly confirm if EMD of Rs.50 Lacs is applicable or not. Incaes applicable, kindly consider to exempt the same. | Contractual | Yes it is applicable.
64 | ITB | 42/533 | 5.1 | ‘Declaration regarding the procurement of Solar Inverters & Solar Modules from class I local suppliers, as per 'Form F-12' | Declaration format is not attached with specs. We would request you to kindly restrict the same to self undertaking only at this stage. | Contractual | Declaration form attached with Amendment 1
65 | ITB | 42/533 | 36.3 | The of “Notification of Award (NOA)"/ “Letter of Intent (LOI)”/ “Letter of Allocation (LOA)” shall be issued to successful bidder in duplicate. The successful bidder is required to return its duplicate copy duly signed and stamped on each page including all the Appendix, Annexures as a token of acceptance. | Kindly let us know the timeline for such mandatory acknowledgment. | Contractual | 07 days
66 | GCC | 93/533 | 19.1 | Force Majeure | Kindly consider as under: Please include epidemic & Pandemic as well 2. Kindly confirm that payments falling due as of event of force majeure shall be released by employer. | Contractual | The terms and conditions of the tender document shall prevail.
67 | GCC | 93/533 | 19.1 | Act of God, including, but not limited to lightning, fire not caused by Contractors’ negligence and explosion (to the extent originating from a source external to the site), earthquake (above 7.0 magnitude on Richter Scale), volcanic eruption, landslide, unprecedented flood, cyclone, typhoon or tornado; | Since their is no scientific evidence justifying quantum of collateral damage on a/c of earthquake in correlation to Richter Scale therefore we would like to request as under: Act of God, including, but not limited to lightning, fire not caused by Contractors’ negligence and explosion (to the extent originating from a source external to the site), earthquake (above 7.0 magnitude on Richter Scale), volcanic eruption, landslide, unprecedented flood, cyclone, typhoon or tornado; | Contractual | The terms and conditions of the tender document shall prevail.
68 | GCC | 93/533 | 19.4 | Upon occurrence of such causes, the party alleging that it has been rendered unable as aforesaid, thereby, shall notify the other party in writing by registered notice within 48 (forty eight) hours of ….............................. | Considering Force Majeure implications are highly uncertain hence kindly modify as under: Upon occurrence of such causes, the party alleging that it has been rendered unable as aforesaid, thereby, shall notify the other party in writing by registered notice within 7 days of the | Contractual | Kindly refer Amendment 1 for the same.
69 | GCC | 94/523 | 20.1 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities. | By 'Contract Value' we understand the value of 1st and 2nd Contract and exclude 3rd(O&M) Please confirm | Contractual | Yes
70 | GCC | 96/533 | 24 | Further, any delay beyond 30 (Thirty) days shall attract interest @ 1.25% per month on the total Contract Performance Security amount, calculated on pro-rata basis accordingly. Owner at its sole discretion may cancel the NOA/ LOI/LOA & forfeit 100% of EMD if applicable, in case Contract Performance Security is not submitted within 45 (Forty-five) days from issuance of NOA/ LOI/LOA. However, total project completion period shall remain same. Part Security shall not be accepted. The Zero Date shall be counted from the date of LOA or NTP whichever is later. | We would request you to kindly delete the provision of interest for delayed submission for PBG as owner is anyway reserving right for cancellation of NOA after 45 days. . | Contractual | The terms and conditions of the tender document shall prevail.
71 | GCC |  | 32.1.2 | The Contractor shall acquire, on behalf of Owner, in the Owner’s name, all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the Country/State where the Site is located that are necessary for the setting up of the Plant & operation of Plant till its desired life as mentioned under the Contract, including, but not limited to, entry permits for all imported Owner’s/Employer’s Equipment (if any). In this regard, any document required from Owner/ Employer shall be intimated at least 10 days prior to submission. Contractor has to ensure safe keeping of the documents and diligent use. It is the responsibility of the Contractor to safe keep and return all the original approvals, permits, licenses, certificates and other relevant document generated as a result of the setting up of project and comprehensive O&M process to the Owner | Contractor shall not be be responsible for the stautory permits which are related employer typically , but not limited to, viz ROW ,ROU ,Transmission line permission ,substation connectivity ,electrical inspector , land related permits etc | Contractual | The terms and conditions of the tender document shall prevail.
72 | GCC | 109 | 38.2 | No adjustment in Contract Price shall be allowed for reasons of such delays and extensions granted except as provided in Tender Document, where the Employer/ Owner reserves the right to seek indulgence of Contractor to maintain the agreed Time Schedule of Completion. In such an event the Contractor shall be obliged for working by Contractor's personnel for additional time beyond stipulated working hours as also Sundays and Holidays and achieve the completion date/interim targets. | Since the delay stated herein is purely due to the employer therefore the contractor is fully entitled for cost compensation on account of such delays including but not limited to site idling charges ,keeping the site safe etc | Contractual | All such instances will be dealt on case to case basis.
73 | GCC | 109/533 | 39 | Payment if the Contract is terminated | Bidder understands that such provision is applicable under both cases i.e. termination under contractor's default & termination under employer's convenience. Kindly confirm. | Contractual | No
74 | GCC | 117/533 | 53.3 | 53.3 Codes and Standards | We would request you to kindly incorporate provision of contract price adjustment due to changes in Codes & Standards , with base date as 7 days before the bid submission. | Contractual | The terms and conditions of the tender document shall prevail.
75 | GCC | 124/533 | 70 | Suspension of Works i) Subject to the provisions of sub-para (ii) of this clause, the Contractor shall, if ordered in writing by the Engineer-in-Charge/Project Manager, or his representative, temporarily suspend the Works or any part thereof for such written order, proceed with the Work therein ordered to be suspended until, he shall have received a written order to proceed therewith. The Contractor shall not be entitled to claim compensation for any loss or damage sustained by him by reason of temporary suspension of the Works aforesaid. However, suitable time extension may be considered at the sole discretion of the owner. ii) In case of suspensions of entire Work, ordered in writing by Engineer-in-Charge/Project Manager, for a period of more than 03 (Three) months, the Contractor shall have the option to terminate the Contract. | Kindly consider as under: 1. Contractor shall be entitled for all costs/ expenses incurred owing to such suspension due to owner. 2. Termination ,post three months of suspension ,should be treated as "Termination due to Employer's convenience" | Contractual | The terms and conditions of the tender document shall prevail.
76 | GCC | 126/533 | 73 | Defects Liability Period [12 (Twelve) Months Period of Liability from the date of Operational Acceptance] | Kindly consider the same as 18 months from commissioning or 12 months from Operational Acceptance which ever is earlier. | Contractual | The terms and conditions of the tender document shall prevail.
77 | GCC | 126/533 | 73.13 | 73.13 Latent defect liability: Notwithstanding, the defect liability period of 12 months above, the plant shall carry a latent defect liability of 5 years from date of operational acceptance towards any design/ manufacturing defects in the equipment supplied by the Contractor | We would request you to kindly elaborate the process for determination for the defect as Latent Defect | Technical | The standard Industry practise would be adopted while determining the deferct as "Latent Defect", which excsludes any defects related to the Workmanship.
78 | GCC | 132/533 | 78.1 | 78.1 If any action is brought before a Court, Tribunal or any other Authority against the Employer/ Owner or an officer or agent of the Employer/ Owner, for the failure, omission or neglect on the part of the Contractor to perform any acts, matters, covenants or things under the Contract, or damage or injury or death caused by the alleged omission or negligence on the part of the Contractor, his agents, representatives or his Sub-Contractor's, or in connection with any claim based on lawful demands of Sub-Contractor's workmen suppliers or employees, the Contractor, shall in such cases indemnify and keep the Employer/ Owner and/ or their representatives harmless from all losses, damages, expenses or decrees arising out of such action. | We would request you to kindly extend identical indemnification to Bidder/Contractor as well | Contractual | The terms and conditions of the tender document shall prevail.
79 | GCC | 133/533 | 80.6 | Schedule of Rates to Cover Risks of Delay The Schedule of Rates shall be deemed to include and cover the risk of all possibilities of delay and interference with the Contractor's conduct of Work which occur from any causes including orders of the Employer/ Owner in the exercise of his power and on account of extension of time granted due to various reasons and for all other possible or probable causes of delay. | We would request you to kindly omit this clause as delays owing to owner shall make contractor eligible for reasonable cost compensation in accordance with the delay so inflicted by owner. | Contractual | All such instances will be dealt on case to case basis.
80 | GCC | 134/533 | 81.1.3 | 81.1.3 Engineer-in-Charge/Project Manager shall pass the bills after carrying out the comprehensive checks in accordance with the terms and conditions of the Contracts, within 21 (Twenty-one) days of submission of the bills along with all necessary enclosures and documents, complete in all respects and send the same to the Owner to effect payment to the Contractor as per the defined payment terms. 81.1.4 Owner shall make all endeavor to make payments of undisputed amount of the bills submitted based on the joint measurements within 30 (Thirty) days from the date of certification by the Engineer-in- Charge/Project Manager. Any disputed claims/amounts will be mutually settled and paid accordingly. | As per the provisions of GCC stated herein , the total processing time of payments i.e. certification + payment release process is ( 21days+30days) 51 days. We would request you to kindly ensure that the same is restricted to 30 days from date of submission of invoice along with necessary supporting documents. | Contractual | The terms and conditions of the tender document shall prevail.
81 | GCC | 136/533 | 88 | 88. Final Decision and Final Acceptance 88.1 Upon expiry of the period of liability & the Works have been duly maintained by the Contractor during monsoon or such period as hereinbefore provided in Clause 73 & 74 and that the Contractor has in all respect duly made-up any subsidence and performed all his obligations under the Contract, the Owner give a final acceptance to that effect and the Contractor shall not be considered to have fulfilled the whole of his obligations under Contract until Final acceptance shall have been given by the Owner not withstanding any previous entry upon the Work and taking possession, working or using of the same or any part thereof by the Owner. | Bidder understands that "Upon expiry of the period of liability " implies "Upon expiry of the period of defect liability ". Kindly confirm? | Contractual | Contracts Liability covers Defect liability along with all other related liabilities on account of functional guarantees, performance etc
82 | GCC | 130/533 | 94.4 | 94.4 In case of any delay of the project attributable to the Contractor, the Contractor himself in consultation with Owner/Employer shall take the extension of insurance. Any financial implications shall be borne by the Contractor. | However in case the delay in project is by employer , the applicable charges for extension of Insurances shall be borne by employer.Pls confirm. | Contractual | All such instances will be dealt on case to case basis.
83 | GCC | 139/533 | 95.3 | 95.3 The Contractor shall indemnify and keep the Employer/ Owner harmless of all claims for damages to property other than Employer’s/ Owner’s property arising under or by reason of this agreement, if such claims result from the fault and/ or negligence or willful acts or omission of the Contractor, his employees, agents, representative of Sub-Contractor. | We would request you to kindly incorporate identical indemnification for contractor from faults/damages attributable to employer | Contractual | The terms and conditions of the tender document shall prevail.
84 | GCC | 145/533 | 100 | Above mentioned Arbitration clause will be applicable for the Disputes where the amount of claim is less than or equal to INR 1Crore (Indian Rupees One Crore only). For the cases of disputes where the amount of claim is more than INR 1 Crore (Indian Rupees One Crore), such disputes will be settled through commercial Courts established under the Commercial Courts, Commercial Division and Commercial Appellate divisions of High Courts act, 2015 | We would request you to kindly remove such capping for Arbitration. | Contractual | The terms and conditions of the tender document shall prevail.
85 | SCC | 154/533 | 10 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning of Plant facilities in accordance with SCC Clause then the Contractor shall pay to the Owner a sum equivalent to one percent (1%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of ten percent (10%) of Contract Price for the whole of the facilities. | Kindly restrict the LD to 0.5% per week prorated to part thereof, of the proportionate uncommission value of contract, subject to maximum of 5% of contract price | Contractual | The terms and conditions of the tender document shall prevail.
86 | SCC | 155/533 | 11 | The value of the Contract Performance Security shall be 4% (Four percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 132 Months (09 Months Project commissioning period) + 120 Months O & M Period + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of one year and the same may be extended every year till completion of the total 132 months period. | 1. We would request you to kindly reduce CPBG to 3%. 2. Pls confirm if Service Contract includes O&M as well. | Contractual | 1. Please refer MNRE Order No F. No. 283/114/2018-GRID SOLAR dated 16.12.2021, wherein the Performance Security is 4% only for the projects wherein the site is specified by the procurer. 2. Service and O&M are two sperate contracts. Kindly refer to IFB (Clause 6) for more details on the same.
87 | SCC | 155/533 | 11 | Further, 5% (Five percent) of each running bill will be deducted as security deposit till the security deposit value becomes 5% of the contract value. This Security deposit will be released to the contractor against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. | Inview of the stringent payment terms, such provision shall further create negative cashflow. | Contractual | It’s a requirement from the Project Owner side & hence, The terms and conditions of the tender document shall prevail.
88 | SCC | 156/533 | 12 | In the matter of connectivity of plant to DISCOM’s substation including bay allocation, etc, the contractor shall acquire all necessary approvals/permissions on behalf of owner. The statutory fees pertaining to such shall be reimbursed by the owner on production of documentary evidence. In this regard, any document - required from Owner/ Employer shall be intimated at least 10 days prior to submission. Contractor has to ensure safe keeping of the documents and diligent use. It is the responsibility of the Contractor to safe keep and return all the original approvals, permits, licenses, certificates and other relevant document generated as a result of the setting up/operating the power plant | We would request you to kindly retain such permits in your scope. Delay in arranging such permits by contractor owing to delays by nodal agencies shall result in delay in execution of project which shall create a LD liability on the contractor. | Contractual | The terms and conditions of the tender document shall prevail.
89 | SCC | 161/533 | 19 | b. ARBITRATION: VOID | Kindly confirm is arbitration provision is applicable for this tender. | Contractual | Pl refer SCC clause 19, which says "Regarding any constructed dispute to be referred to the Conciliation and Settlement Committee for resolution, the procedure for reconciliation and settlement shall be followed as per the guidelines issued by the Ministry of Shipping, Ports, and Waterways. (Ref. CONCILIATION AND SETTLEMENT GUIDELINES dt 05.10.2021)" & Arbitration louse is not applicable
90 | SOW | 235/533 | 7 | 7 Statutory Approvals | We would request you to kindly retain such permits in your scope. Delay in arranging such permits by contractor owing to delays by nodal agencies shall result in delay in execution of project which shall create a LD liability on the contractor. | Contractual | The terms and conditions of the tender document shall prevail.
91 | BDS /ITB | 9 | 9_5.3 | Only Bid Securing Declaration is to be submitted in line with the form as attached under Section VI, “Sample forms & formats” The Tender Processing Fee and EMD, if applicable is exempted for MSME Vendors registered under NSIC/ Udyog Aadhaar/DIC Category only. In order to avail the exemption in Tender Processing Fee in case of consortium/ JV, all the members should be registered as MSME Vendors under NSIC/ Udyog Aadhaar Category/DIC. | We are MSME registered company having Udyam registration certificate. As per Tender Clause we are exempted for EMD fees OR we have to give the Bid Security Declaration alongwith the Bid. | Contractual | EMD is exempted for MSME's. Kindly check the amendment 1 for more details on the same.
92 | SOW,Cl:7_Statutory Approvals | 12_17 | 1 | Obtaining statutory approvals /clearances/ compliances on behalf of the Employer from various Government Departments is the Scope of Bidder | Please confirm the reimbursement of statutory Approval fees. | Contractual | Its is in the contractor's scope only.
93 | SOW,Cl:7_Statutory Approvals | 12_17 | 7 | Costal Zone Clearance Approval | As the Above Port is comes under Coastal Area please confirm the CRZ Clearance. | Technical | The Contractor shall acquire CRZ clearance on behalf of owner. VOCPT will facilitate.
94 | SOW, | 4_17 | 1 | Interconnecting Substation - Interconnecting Substation Tuticorin Auto 230/110/22 kV Substation, Muthaiapuram | Please confirm the given substation is of Port Or it is nearby substation. | Technical | The substation belongs to TANGEDCO.
95 | SCC | 5_11 | 11 | The value of the Contract Performance Security shall be 4% (Four percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 132 Months (09 Months Project commissioning period) + 120 Months O & M Period + 03 Months additional) from the date of its issuance. | As per Central Government Guidelines the PBG should be 3%. We request you please consider PBG @ 3% for SITC Contract & which should be valid till Completion Period also please accept PBG for O&M Contract separately. | Contractual | 1. Please refer MNRE Order No F. No. 283/114/2018-GRID SOLAR dated 16.12.2021, wherin the Performance Security is 4% only for the projects wherein the site is specified by the procurer.
96 | ROW 4.13 (Page No. 230) SOW(7 OF 17) | 230 _ | 4.13 | Right of Way | Design & construction of Transmission line/ cable from plant take off point to the designated substation including right of way (ROW). –Please specify scope | Technical | Solar plant location is with in VOCPT premises. The area from proposed solar power plant location up to the boundary of VOCPT belongs to VOCPT. The area beyond VOCPT boundary and up to the substation is under Public/Private domain. Tentative route map of transmission line is attached for reference (Annexure-H of Section-VII ). ROW required for the area beyond VOCPT boundary and upto the substation is in the scope of the Contractor.
97 | Transmission Line 4.13 Page No. 230 | 230 _ | 4.13 | Transmission Line | Please specify scope of approval for laying UG cable from an existing railway siding of SPIC Chemical factory | Technical | Permissions need to be taken from Railways Department.
98 | AC Cable 7 TS Page 36 of 112 (Page No. 276) | 7 | 36 of 112 (Page No. 276) | AC Cable - Aluminum Cable | Please clarify use of Aluminum cable For AC side | Technical | The referred clause does not specifically mention the conductor material. Conductor material that conforms the technical specifications may be used.
99 | General | _ | _ | General | Please clarify, what will be the zero date of the site. The zero date must start after the acceptance of availability of clear land. | Contractual | Issuance of NOA is considered as the zero date as mentioned in SCC (clause 3).
100 | General | _ | _ | Reverse Power Relay for DG | Please confirm scope for Reverse Power relay for DG | Technical | It is assumed that the 'DG' mentioned in the query means Diesel Generator. Diesel Generator is not in the scope of the tender.
101 | General | _ | _ | Inverter & ACDB Location | Please clarify placing of Inverter & ACDB location as per site requirement | Technical | Location of inverter and ACDB will be decided during detailed engineering.
102 | General | _ | _ | SLD | Please share the SLD of Switchyard. | Technical | 22 kV bay has to constructed by the Contractor at the interconnecting substation. Kindly visit the substation for existing SLD.
103 | General | _ | _ | Change in Law | If, after the date of Bid submission, any law, regulation, ordinance, order or by-law having the force of law is enacted, promulgated, abrogated, or changed, which shall be deemed to include any change in interpretation or application by the competent authorities, that subsequently affects the costs and expenses of the Contractor and/or the Time for Completion, Contract Price shall be correspondingly increased or decreased, and/or the Time for Completion shall be reasonably adjusted to the extent that the Contractor has thereby been affected in the performance of any of its obligations under the Tender | Contractual | Kinldy refer clause 51 of GCC for more clarity on the mentioned clause.
104 | General | _ | _ | ROW | ROW issues will not be in our scope. Please confirm | Technical | ROW is under the Contractor's scope.
105 | General | _ | _ | Soil Report | Please provide Geo-Tech report of the notified land if available | Technical | Soil testing report of nearby land is provided in 'Annexure-I of Section-VII' for reference. No warranty is expressed or implied that such information, given in good faith, will represent a complete or accurate picture of the whole of the site. The Contractor shall be responsible for any inference it may draw from such information. The Employer shall not be responsible for any variations in soil characteristics, if observed, during detailed soil investigation to be carried out by the Contractor during contract execution and there shall be no compensation what so ever in the contract price on this account.
106 | General | _ | _ | Metering/Billing Point | Please confirm billing point high voltage level i.e. 22kVor else | Technical | Metering point for CUF measurement will be 22 kV side of interconnecting substation.
107 | General | _ | _ | Land | Please confirm the status of the notified Land. Whether the given land is NA/Forest. Also, please confirm if any conversion is required. | Technical | VOCPT owns the land. There is no need for convertion.
108 | SCC | _ | _ | _ | As per tender, It was stated that working capital must be INR 6,27,50,000. We are able to submit the solvency upto 6.28 Cr. Is it acceptable instead of working capital. We will provide the letter from the bank stating that solvency upto 5C. Is it acceptable from your end? | Contractual | If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal INR 6,27,50,000/- (Indian Rupees six crores twenty-seven lacs & fifty thousand only) to meet the working Capital requirement of this particular Project.
109 | SOW | 235/533 | 7 | Statutory approvals- Open access | Please confirm if we have to get all the permissions for open access for this plant | Contractual | Yes
110 | IFB | 11/533 | H | EMD | Please confirm if EMD is exempted for MSME units | Contractual | Yes it is exempted for MSME's registered under NIC/Udyog Aadhar/DIC
111 | IFB | 11/533 | I | Tender Processing fees | Please confirm if tender fees is exempted for MSME units | Contractual | Yes it is exempted for MSME's registered under NIC/Udyog Aadhar/DIC
112 | SOW | 233/533 | 5.13 | Railway crossing | Please confirm the specifications and requirements bidder has to take care during the work at railway crossing. | Technical | Kindly refer Clause 5.13 of Scope of Works. Detailed specifications shall be as per Railways Department.
113 | SECTION - VII B. TECHNICAL SPECIFICATIONS | 249 | 1.3 | 1.3 Supplier Qualification Criteria The PV Module Supplier should have supplied minimum 5 GW capacity globally or 500 MW in India in the past 5 years (as on last date of Bid submission). The PV Module Supplier shall be Class-I local supplier as per MNRE Order on Public Procurement (Preference to Make in India) to provide for Purchase Preference (linked with local content) in respect of Renewable Energy (RE) Sector dated 9th February, 2021 and subsequent amendments. | Request seeking SECI to relax in Supplier Qualification Criteria: We request you to kindly amend the clause as per below : SPV Panel : The PV Modules Supplier should have supplied minimum 1 GW capacity globally or 100 MW cumulative Capacity in India in the past 5 years (as on last date of Bid submission). | Technical | The terms and conditions of the tender document shall prevail.
114 |  | 11 | K | Site Visit: Prospective Bidders are advised to visit the proposed Land site to study the actual conditions and go through the plans/ drawings connected to the present scope of work etc including power evacuation system and Ground based Project capacities and get acquainted with the same before attending Pre-bid meeting. For seeking visit of site or any clarifications bidders may contact the AGM, PV SECI. | We request you to kindly provide the contact person details for site Visit (Name and Mobile No.) | Contractual | Mr ISK Reddy : Mob No 8130473483
115 | II | 25 | 12.6 | However, Change in Law shall not include (iii) any change on account of regulatory measures by the Appropriate Commission. | EPC contractor cannot be made liable for any change in the regulatory laws which can affect his costing post bid submission. EPC contractor bids on the basis of current laws enforce and as such takes into account all charges with it. If charges change after bid submission, it should be paid by the Owner and covered in this clause. | Contractual | The terms and conditions of the tender document shall prevail.
116 | IV | 119 | 58.1 | Contractor shall deliver supplies at site in accordance to its erection sequence. Owner may hold payment against supplies in case same is delivered more than 03 (Three) months before its erection requirement (except for imported items) | Supply of items at site cannot be timed as per the erection sequence as various factors like availability of items, pricing, transportation etc. have to be factored in whilst delivering items at site. Request remove clause of holding of payment for 03 months which restricts the Contractor to plan for the project in terms of his financial/commercial requirements. | Contractual | The terms and conditions of the tender document shall prevail.
117 | IV | 120 | 59.3 | Owner, at his sole discretion and upon request from Contractor, may provide appropriate space for storage outside the site on chargeable basis mutually agreeable to both parties. | Mutually agreed rates may increase chances of dispute which can result in delay of project timeline. Please provide exact charges for the above. | Contractual | This may not be feasible at this point of time & same may be agreed before hadn with the successful bidder only.
118 | IV | 125 | 73 | Defects Liability Period [12 (Twelve) Months Period of Liability from the date of Operational Acceptance] | This contractor has to carry out comprehensive O&M of the plant for a period of 10 years on operational acceptance of the plant which includes attending to all defects and defects in the design, engineering, materials and workmanship of the Plant and Equipment supplied and of the work executed. All the requirements mentioned in this clause is already covered in the O&M scope. There is therefore no requirement of a separate DLP clause. As per clause 73.16 contractor has to guarantee workmanship of the plant for 5 years which whereas in clause 73 he has to guarantee the plant workmanship for 12 months. Please clarify. | Contractual | The terms and conditions of the tender document shall prevail.
119 | IV | 129 | 76.2.3 | Upon completion of the construction activities/ O&M activities, the Contractor shall obtain no – objection certificate (NOC) from local/ statutory bodies in respect to the fulfillment of all compliance and submit a copy to the Owner prior to the final settlement | Kindly be specific about the NOC's to be obtained from which all authorities as it seems to be open ended. | Contractual | As such all related NOC's required for the project are to be obtained by the contractor itself
120 | IV | 135 | 84.2 | Engineer-in-Charge/Project Manager shall review such claims within a reasonably period of time and cause to discharge these in a manner considered appropriate after due deliberations thereon. However, Contractor shall be obliged to carry on with the Work during the period in which his claims are under consideration by the Owner, irrespective of the outcome of such claims, where additional payments for Works considered extra are justifiable in accordance with the Contract provisions. | Project Manager should review the claim in a specific time period which should be notified here. The Contractor should given be a go-ahead for extra work commencement only after it is accepted by the owner as extra work. This clause is not addressing the Contractor's concern of accepting the work. If after carrying out the work, the Project Manager decides that it is not extra work then it will be unfair to the contractor. This is with regard to only extra works and not the regular contracted work. Kindly amend the clause. | Contractual | The terms and conditions of the tender document shall prevail.
121 | IV | 120 | 58.4 | The Employer/ Owner will insist on the procurement of materials which bear ISI stamp and/ or which are supplied by reputed suppliers. | Kindly specify the reputed make suppliers for each item which the employer may suggest to avoid any ambiguity later on during the execution time. The word "Reputed make" is too broad. Suggest give accepting condition for acceptance of the material. However, please note that such clauses will only delay the project as there are bound to be disagreements between the contractor and the Employer view ambiguous wordings in the Tender. | Technical | The suppliers who qualifies the technical specifications are reputed suppliers. The terms and conditions of the tender document shall prevail.
122 | IV | 123 | 67.1 | However, in case re-inspection is necessitated on account of nonacceptance of item(s) due to failure on Factory Acceptance Test(s), the cost of associated travel and accommodation borne by the Employer/Owner shall be on account of the Contractor. | It will be the endeavor of the contractor to complete the acceptance of the tests in one visit at the factory, however, this clause is ambiguous as it does not specify as to what all can be attributed to the contractor for non acceptance of the material. Kindly be specific about the conditions under which the Contractor can be held liable. Also, please give a clear list of equipment which will be inspected at Factory. | Technical | Major equipmets like Modules, inverters, MMS, transformer, Switchgear panel etc. would be inspected by employer/owner at factory. Any deviation from the approved manufacturing quality plan would be considered as non acceptance of the material. The terms and conditions of the tender document shall prevail.
123 | IV | 134 | 81.1.3 | Engineer-in-Charge/Project Manager shall pass the bills after carrying out the comprehensive checks in accordance with the terms and conditions of the Contracts, within 21 days of submission of the bills, complete in all respects and send the same to the Employer/ Owner to effect payment to the Contractor as per the defined payment terms. | Suggest Engineer-in-charge to forward the bills to employer for payment within 3 days after due verification. 21 days is too long for verification time. If we take Clause 81.1.3 and 81.1.4 together then the max time the employer can take for payment of bill would be 40 days from the date of submission of bills which is heavily biased in favor of the Employer | Contractual | The terms and conditions of the tender document shall prevail.
124 | IV | 134 | 81.1.4 | Employer/ Owner shall make all endeavor to make payments of undisputed amount of the bills submitted based on the joint measurements within 30 (Thirty) days from the date of certification by the Engineer-in-Charge/Project Manager. | Suggest amend the payment to be made within 15 (fifteen) days from the date of certification. | Contractual | The terms and conditions of the tender document shall prevail.
125 | IV | 139 | 94.5 | The Contractor should arrange for providing insurance coverage to its workmen under Workmen’s Compensation Act or similar Rules and Acts as applicable during execution of work for covering risk against any mishap to its workmen. | As per clause 94.10, the contractor is to provide ESIC for all workers which covers all risks/accidents in case of any mishap at site. Insurance coverage as per clause 94.5 shall be provided for Contractor's personnel working on site who are not covered under ESIC. Please confirm. | Contractual | Yes
126 | IV | 146 | 103.1 | In respect of all labor, directly employed in the Work for the performance of Contractor's part of this agreement, the Contractor shall at his own expense arrange for all the safety provisions as per safety codes of C.P.W.D., Indian Standards Institution. The Electricity Act, The Mines Act and such other acts as applicable. | Please clarify the applicability of "The Mines Act" in this work. This is a construction contract and hence applicability of this act is not understood. Please clarify the applicability of this act in context of this tender. | Contractual | It’s a standard EPC document of SECI wherein all general clauses are covered.
127 | IV | 159 | SCC Page 8 of 12 Part-C | Final Ten percent (10%) payment of Civil Works shall be paid against submission of the BG of the equivalent amount & against the Operational Acceptance of the plant Facility pursuant to successful Guarantee Tests and demonstration of Performance Ratio (PR) including submission of all as-built drawings and O&M manual. This BG shall be valid for a period of 18 (Eighteen) months from the date of its issuance & will be released after CUF demonstration on completion of first year of O&M, pursuant to the submission of all requisite documentation up to the final acceptance of the Plant facilities. However, in case of any delay, the BG shall be extended suitably. | Request include a separate chapter/section on the documentation required for clearing the contractors bills. It has been our experience that new requirements are projected as there is no clarity on the exact documents required to be submitted along with the bills. This delays contractors bill payments leading to financial crunch and Please clarify specifically what are the "requisite documentation" as mentioned in the clause. | Contractual | The terms and conditions of the tender document shall prevail.
128 | VII | 254 | 3.3 | DC cables ( SMU to Inverter) shall be single core, armored, Flame Retardant Low smoke (FRLS), PVC outer sheath conforming to IS 7098-I. | Generally, Solar DC Cable have flame retardant properties but for XLPE Armored Cables from SMU to Inverter. Request to remove FRLS requirement for this cable. | Technical | The terms and conditions of the tender document shall prevail.
129 | VII | 254 | 3.5 | The average voltage drop in the cables (Modules to Inverter) shall be limited to 1.5 % of the rated voltage. | We understood that the voltage drop will be limited to 3% of the rated voltage at nominal condition (from PV Module to Inverter). Request Confirm. | Technical | The terms and conditions of the tender document shall prevail.
130 | VII | 257 | 4.3.1 | The rated/ name plate AC capacity of the PCU shall be AC power output of the PCU at 50°C. | Inverter supplier gives the rating on its number plate at 25o /40o C which is a standard practice. Request accept rating at 40o C. | Technical | The terms and conditions of the tender document shall prevail.
131 | VII | 276 | 7.2 | All AC cables shall be flame retardant, low smoke (FRLS) type designed to withstand all mechanical, electrical and thermal stresses develop under steady state and transient operating conditions. | Generally, for all AC Cables, there is no requirement of FRLS properties. Request to remove FRLS requirement for XLPE armored cables. | Technical | The terms and conditions of the tender document shall prevail.
132 | VII | 287 | 12.3.3 | Continuous copper Earthing wire shall be run to connect a group of modules and both ends of the loop shall be bolted to the DC earth grid using bimetallic lugs and stainless-steel fasteners. The copper Earthing wire shall be routed in such a way to avoid physical contact with the module aluminum frame. | If module manufacturer approves that Earthing is achieved by continuous MMS, then request to remove separate module to module Earthing requirement using Cu wire. | Technical | The terms and conditions of the tender document shall prevail.
133 | VII | 289 | 13.2 | Protection Level for the entire plant shall be level – III. | Generally, protection level is selected based on lighting protection risk analysis & for this site location Level-IV is also sufficient. Request client to confirm that the protection level shall be decided during the detailed Engineering. | Technical | The terms and conditions of the tender document shall prevail.
134 | VII | 290 | 14.1.5 | All testing of the optic fiber cable being supplied shall be as per the relevant IEC, EIA and other international standards. | Request waive off requirement of Test certificates for OFC and RS 485 cables as suppliers/dealers are unable to provide type test certificates for small quantities of cables. Also kindly provide specific vendor list for OFC and RS485 cables . | Technical | The terms and conditions of the tender document shall prevail.
135 | VII | 300 | 16.4.8 | Lighting panels shall be earthed by two separate and distinct connections with Earthing system. Switch boxes, junction boxes, lighting fixtures, fans, single phase receptacles etc. shall be earthed by means of separate earth continuity conductor. Cable armour shall be connected to Earthing system at both the ends. Proper Earthing of street light poles shall be ensured. | Street light pole, junction box and lighting fixtures are metallically connected. Therefore separate Earthing is not required for each component of the pole. The junction box will be earthed by using PEN method at lighting panel. Request client to clarify and confirm. | Technical | It is not necessary to earth each component of the light pole separately; all the components of the light pole may be bonded together and earthed. The terms and conditions of the tender document shall prevail.
136 | VII | 297 | 16.3.2 | The lighting system for outdoor and indoor areas of solar power plant shall be designed in such a way that uniform illumination is achieved. Average LUX level to be maintained in different areas shall be as under: Control Room and equipment rooms- 300 LUX Office- 300 LUX Battery & other rooms - 150 LUX | Request propose amendment to LUX level requirements in following rooms as follows based on practical experience : Office- 200 LUX | Technical | The terms and conditions of the tender document shall prevail.
137 | VII | 298 | 16.3.3 | The lighting level shall take into account appropriate light output ratio of luminaires, coefficient of utilization maintenance factor (of 0.7 or less) to take into account deterioration with time and dust deposition. | The mentioned coefficient of utilization maintenance factor (of 0.7 or less) for conventional lights like Halogen, CFL, etc. Generally for LED lights it shall be 0.9 or less. Request Client to change this coefficient of utilization maintenance factor as 0.9 or less by considering above. | Technical | The terms and conditions of the tender document shall prevail.
138 | VII | 299 | 16.4.1 | LED luminaires shall meet the following parameters: Luminaire efficacy >90 lumens per watt Color Temperature 5700o K (cool day light) | Request client to change this parameters as follow. Luminaire efficacy > = 90 lumens per watt Color Temperature 4000o K (cool day light) Cool day light temperature of LED is around 4000 o K to 4500 o K. For your information, at 5700 o K, it will be bluish light instead of cool day light. | Technical | The terms and conditions of the tender document shall prevail.
139 | VII | 331 | 16.1.2 | Inverter, Switchgear panel, Metering panel and associated equipment shall be installed on plinth as open installations. The plinth supporting the ICR/LCR equipment shall have RCC framed structure with foundations, columns and beams built up to the plinth level (FFL). Plinth filling shall be provided as per the specifications for the same stipulated by the Clause No. 21 in Section VII-B of the tender document. Flooring shall be provided using 40 mm thick Cement concrete (IPS) flooring (1:2:4), aggregate size 10 mm down, conforming to IS 2571 with 2mm thick Heavy duty epoxy coating (Industrial grade) of approved make on top as per manufacturer specifications. There shall be suitable provision for easy passage of O&M personnel, cable trench, operating area, etc. as required. Weather canopy shall be provided for all open installations. Canopy columns shall be supported on pedestals at plinth level. | In case of outdoor inverter & Switchgear, request client to confirm if use of pre Engineering building/shed for data logger, UPS, battery or other indoor components is allowed. | Technical | Kindly refer S.No.3 of Amendment-1.
140 | VII | 332 | 16.2.1 | For O&M of SPV Plant MCR building shall provide following facilities; (I) Inverter/ Switchgear, equipment room(s) as per requirement (ii) Air conditioned area (with provision of split A/C unit of adequate capacity) for SCADA room (min. 12m2) & Conference room ( min. area 20m2) (iii) Supervisor cabin and office area (min. area 25m2) (iv) Store cum record room (min. area 20m2) (v) Battery room as per requirement & (vi) One toilet block with gents and ladies wash room facilities (min. area 12m2) (vii) There shall be suitable provision for easy/ smooth passage for O&M personnel, cable trenches etc. | We understood that the minimum area given at this clause is tentative & can be reduced based on practical requirement during detailed engineering. Request client to confirm for the same. | Technical | The terms and conditions of the tender document shall prevail.
141 | VII | 325 | 11.3 | Min. depth of foundation for all buildings and plinth for open installations shall be 1.5 m below NGL. For all other structures, min. depth of foundation shall be 1.0 m unless specified otherwise. | Request client to confirm the depth of the SMB/SJB foundation depth in case hard rock area is encountered. | Technical | The terms and conditions of the tender document shall prevail.
142 | VII | 325 | 11.5 | All design & drawings shall be submitted to the Engineer for approval before execution. | Request client to confirm the maximum time period of 10 (Ten) days for GFC drawing/document approvals. | Technical | Kindly refer Clause 55.3 of GCC.
143 | IV | 113 | 45.3 | Breakdown / Corrective maintenance: Whenever a fault occurs, the Contractor has to attend to rectify the fault & the fault must be rectified within the 72 hours from the time of occurrence of fault. The Contractor must maintain all the records pertaining to all such faults and necessary measures taken. The date of Comprehensive Operation & Maintenance Contract period shall begin from the date of Operational acceptance. However, operation of the Power Plant means operation of system as per TS and workmanship in order to keep the project trouble free covering the O&M period. The Contractor must demonstrate the committed CUF at the end of every year in accordance with commitment made in line with the Performance guarantees. | Irradiance & temperature variation are a major factors to estimate CUF. So, request client to consider the 72 Hrs. downtime as included in CUF calculation as deemed generation. | Technical | The terms and conditions of the tender document shall prevail.
144 | VII | 247 | 2.7 | The designed array capacity at STC shall be suitably determined to meet the proposed guaranteed generation output at the point of interconnection by the contractor in his bid. The contractor shall take care of first year degradation also by installing additional DC capacity as the CUF calculations will not factor the first-year degradation of the modules. | We understand that first-year degradation of modules will be start from date of plant commissioning, kindly confirm. | Technical | Annual degradation of 0.7% will be considered in the calculation of CUF from second year of O&M, i.e. one year after operational acceptance of the plant. No degradation will be considered for calculation of first year CUF. Kindly refer Clause 1(C) in Page No. 38 of O&M Agreement (Annexure-G of Section VII). The terms and conditions of the tender document shall prevail.
145 | VII | 247 | 2.8 | Each component offered by the bidder shall be of established reliability. The minimum target reliability of each equipment shall be established by the bidder considering its mean time between failures and mean time to restore, such that the availability of complete system is assured. Bidder’s recommendation of the spares shall be on the basis of established reliability. | Request client to give the required spares list for each site location as the perception of both the parties can be vastly different and this part has a financial effect on the Contractor. | Technical | Kindly refer 'Annexure-E of Section-VII'. The terms and conditions of the tender document shall prevail.
146 | VII | 258 | 4.4.8 | Dedicated communication interface shall be provided to monitor the PCU from SCADA. | We understood that, PCU unit input will be maximum 16 -Tag (Inputs) per inverter will be considered and without ON/OFF command | Technical | The number of tags will be finalized during detailed engineering. The terms and conditions of the tender document shall prevail.
147 | VII | 262 | 5.2 | Technical Requirements- Tap Changer OCTC, No. of steps shall be as per system requirement | We understood "OFF LOAD TAP CHANGER" (in lieu of OCTC). Kindly confirm. | Technical | OCTC shall mean Off-Circuit Tap Changer. The terms and conditions of the tender document shall prevail.
148 | VII | 265 | 5.6.1.1 | Type Tests (I) Lightning impulse (Full & Chopped Wave) test on windings as per IEC 60076-3 (ii) Temperature Rise test at a tap corresponding to maximum losses as per IEC 60076-2 | In case Transformer supplier has conducted type test(s) within last ten years, he may submit the type test reports to the owner for waiver of conductance of such type test(s) again. These reports should be for the tests conducted on the equipment similar to those proposed to be supplied under this contract and test(s) should have been either conducted at an independent laboratory or should have been witnessed by a client. Kindly confirm. | Technical | Kindly refer S.No.12 of Amendment-1.
149 | VII | 270 | 6.5.2 | The relays shall be capable of operating continuously between 80 – 120% of auxiliary voltage. | Kindly reconsider the really operating voltage limit from 24V-110V DC | Technical | The terms and conditions of the tender document shall prevail.
150 | VII | 281 | 9.3.13 | Earth leakage relay with Core balance CTs (CBCT) shall be provided on main incoming feeders having phase CT ratio more than 50/1A. CBCT's shall be circular window type with window size based on the overall diameter of the cables, to be finalized during detailed engineering. | Instead of providing CBCT, we can use overcurrent relay in LT panel. Kindly confirm | Technical | The terms and conditions of the tender document shall prevail.
151 | VII | 287 | 12.3.2 | Each PV Module frame shall be earthed using copper wire of sufficient cross section. The copper wire shall be connected to the earth hole provided in the module frame using suitable arrangement in line with the manufacturer recommendation. The Earthing arrangement shall use stainless washers to prevent galvanic corrosion between aluminum frame and copper wire. In order to achieve effective Earthing, serrated washers shall be employed to penetrate the anodization layer of the module frame. | The PV module is connected with galvanized MMS structure and same table is connected with grid Earthing .We understood that separate Earthing is not required for PV modules. Kindly confirm. | Technical | The terms and conditions of the tender document shall prevail.
152 | VII | 302 | 18.1 | CCTV Cameras along with monitoring stations (sufficient numbers) and all other accessories required for its proper operation must be installed to have complete coverage of following areas for 24 hours. (I) Main entry: Covering all the entry/exit (ii) Along the Plant Perimeter: Covering complete perimeter of Plant Area to capture all possible intrusion (iii) Control Rooms: Covering Entry/Exit and Equipment Rooms (iv) Switchyard | We understood that one CCTV camera for each mentioned location except in Perimeter. Kindly confirm | Technical | Number of cameras shall be such that complete coverage of all the areas mentioned in the clause is fulfilled. The terms and conditions of the tender document shall prevail.
153 | VII | 342 | 32.1 | The Contractor shall design & provide soak pit and septic tank for treatment of sewage and waste water from MCR building and Security Room. The design of the septic tank shall conform to IS 2470 (Part 1). However, in case of ground water within 1.5m of finished grade level or the soil strata being of low permeability (permeability ≤ 10-6 m/s) where septic tank and soak pit arrangement is not effective, suitable packaged sewage treatment plant of reputed make/manufacture shall be provided. The sewage treatment facility shall be of required capacity and of proven design suitable for total of 15 people. | Request consider pre-fabricated RCC septic tank to reduce execution time and ease of installation with long life. | Technical | Pre-fabricated RCC septic tank conforming to all technical specifications including design consideration as per tender document may be permitted. The terms and conditions of the tender document shall prevail.
154 | VII | 343 | 33.3 | Internal trenches (inside buildings) shall be provided with chequred plate (min. 8mm thick with stiffening angle ISA 50x50x6 @ 750 mm c/c for trench width greater than 800 mm) covers while external trench shall have precast concrete covers. | Kindly change the chequer plate thickness from 8mm into 6mm for safe manual access by O&M individuals. | Technical | The terms and conditions of the tender document shall prevail.
155 | VII | 343 | 34.3 | In case of transformer oil tank capacity more ≥ 20000 liters, the soak pit shall be connected to a separate burnt oil pit through discharge pipe (300 mm dia) and shall be suitably sized to accommodate full oil volume (excluding free board above inlet pipe) of the transformer connected to it, without backflow. In this case the capacity of the soak pit may be reduced to min. 1/3rd of the total transformer oil volume. The burnt oil pit shall be further connected to oily water drainage system. The water shall be discharged into the nearest drain by gravity | We understood that transformer oil soak pit will be precast RCC tank. Kindly confirm | Technical | The terms and conditions of the tender document shall prevail.
156 | VII | 345 | 35.7 | The module cleaning system shall include construction of RCC tank or supply and installation of Ground mounted PVC tank (s) of required storage capacity, pumps (including 1 No. standby pump), water supply mains and flexible hose pipes, taps, valves (NRV, Butterfly valve, Ball valve, Gate valve, PRV, scour valve etc.), Water hammer arrester(s), pressure gauge, flow meter etc. as per the planning & design. | We understood that PVC tank can be used to store water for module cleaning system. Kindly confirm. | Technical | The referred clause allows both RCC and PVC tank. The terms and conditions of the tender document shall prevail.
157 | VII | 309 | 1.2 | This excludes design, supply and installation of Galvanized 220 kV and 132 kV Transmission Line towers, Tower extensions & accessories and 11 kV, 22 kV, 22kV & 33 kV transmission poles & accessories which shall be designed following latest guidelines of respective SEB (State electricity board) and got approved before execution. In absence of SEB/ STU guidelines REC (Rural electrification corporation) standards may be followed. Poles at corner with angle > 100 shall be provided with 4-pole structure or lattice tower. Use of PCC spun poles is not acceptable. Approved copies of these designs & drawings shall be submitted to the employer for reference and record. | As per clause 6.1.1 page no. 206, All statutory approvals/permissions and/or No Objection Certificates (NoC) etc. from the DISCOM for obtaining connectivity at the substation as per Project Particulars provided above. The type of Transmission line pole will be provided as per DISCOM approved drg./specifications. Contractor shall be allowed to use RCC pole if DISCOM approves RCC pole for power evacuation. Kindly confirm. | Technical | The terms and conditions of the tender document shall prevail.
158 | VII | 231 | 4.27 | CCTV cameras for plant surveillance. The CCTV connectivity is to be linked with surveillance monitoring system of VOCPT Admin Building. | Requesting client to give the distance between solar plant to admin We understand that ,there is no addition requirement of display (LCD/LED TV) in admin building . | Technical | CCTV surveillance facility shall be provided at port administrative building with suitable client setup including display. Distance will be 1 km approx. The terms and conditions of the tender document shall prevail.
159 | VII | 328 | 13.14 | The purlins shall be provided with min. following tie/sag rods or angles or channels | Our understanding is that Sag rods are not required for the purlins considering the lateral restrained provided by the solar panels to the purlins. Request client to confirm that our understanding is correct and sag rods are not required for the purlin | Technical | The terms and conditions of the tender document shall prevail.
160 | VII | 326 | 13 | Module Mounting Structure (MMS) | (a) Request client to confirm that during design stage of MMS structure we can utilize IS875 Part III 2015 - latest edition standard including the reduction factor specified within code for calculating the wind loads considering the height and other parameters for MMS structure. (b) Request allow use of Posmac and Galvalume sections in the MMS with minimum thickness of 1 mm. (c) Request allow use of SS304 (or equivalent) fasteners for module mounting and GI fasteners for rest. | Technical | (a) Kindly refer Clause 10.10.3 of 'Technical Specifications-Civil, Mechanical and Plumbing Works'. The terms and conditions of the tender document shall prevail. (b) The terms and conditions of the tender document shall prevail. (c) The terms and conditions of the tender document shall prevail.
161 |  | 105 | 32.1.3 | Contractors responsibility | The grid connectivity permission is one of most important document having bearing on cost and timeline of the project. We request to rpovide the same well before Bidding date . | Technical | The Contractor shall acquire all necessary statutory approvals/permissions on behalf of owner. VOCPT will facilitate. The terms and conditions of the tender document shall prevail.
162 | IV | 93 | 19 | Force Majeure | Restrictions due to Covid 19 Pandemic must be included in Force Majeure clause as due to the pandemic/m restrictions transpiration/ movement of man & material impacted | Contractual | The terms and conditions of the tender document shall prevail.
163 | VII | 259 | 4.4.10 | String inverter, if installed in open, shall be placed inside a canopy shed with at least 15 cm in all directions. Alternatively, the Contractor may install the inverter on the column post of the Module Mounting Structure, below the modules. In such case, the canopy is not required, and the column and foundation shall be designed accordingly. | Canopy Dimension should be as per the OEM guidelines. Please clarify | Technical | The terms and conditions of the tender document shall prevail.
164 | VII | 267 | 6.2 | Technical Parameters - Internal Arc Classification Rating | It should not be compulsory instead it should be as per the OEM design specification. Please clarify | Technical | The terms and conditions of the tender document shall prevail.
Queries Related to Site Survey
1 |  |  |  |  | Please provide the transmission line rout survey including underground cable rout. Please also show the rout on Google earth. | Technical | Provided in tender document
2 |  |  |  |  | Total Area available (Please share the google as well as real image oh the site and demarcate the area on the proposed land) | Technical | Provided in tender document
3 |  |  |  |  | Situation of the Land (Plain / Hilly / Un Even) | Technical | Plain
4 |  |  |  |  | Ground Water depth | Technical | Refer Geo-tech report provided in tender document. It is also recommended for the site survey to get details.
5 |  |  |  |  | Any River/Pond/Natural drain running through the land | Technical | It is recommended for the site survey to get the details.
6 |  |  |  |  | If any River/Pond/Natural drain is running then possibility of diverting is there. | Technical | It is recommended for the site survey to get the details.
7 |  |  |  |  | Type of soil (Sandy / Rocky / Black Cotton / Laterite) | Technical | sandy
8 |  |  |  |  | Nature of soil (Cohesive / Non Cohesive) | Technical | non cohesive
9 |  |  |  |  | Type of Approach road and approx. length (Bitumen / WBM / Murrum / PCC) | Technical | Bitumen
10 |  |  |  |  | Width of approach road. | Technical | Approximately 7m-8m
11 |  |  |  |  | Tentative undulation | Technical | plain
12 |  |  |  |  | Water logging occurs after rain or not? | Technical | no
13 |  |  |  |  | Type of land (Residential / Industrial / Agricultural) | Technical | Industrial
14 |  |  |  |  | Surrounding boundary of the site | Technical | one side is sea, and the other three sides are land.
15 |  |  |  |  | HFL (High flood level) of Land | Technical | Highest High Water Level at Tuticorin w.r.t chart datum is +1.26m and the Mean Sea Level at Tuticorin w.r.t chart datum is +0.64m.
16 |  |  |  |  | Any obstacles (Tree, any constructed building etc…) on installation location, if yes then details. Scope of removals | Technical | the area is Shadow free and completely available for Solar PV plant
17 |  |  |  |  | Plant access. | Technical | Refer clause no. 1.1 of section VII
18 |  |  |  |  | Presences of natural water body in installation location, if yes then details. | Technical | no
19 |  |  |  |  | Natural drain discharge point, if yes then details. | Technical | It is recommended for the site survey to get the details.
20 |  |  |  |  | Any transmission line in installation location, if yes then details. | Technical | No
21 |  |  |  |  | Any pipeline (Gas/Water/other) running in install location, if yes then details. | Technical | No
22 |  |  |  |  | Please mark in proposed land with length and photograph of existing lines / cables which may damage while working at site. | Technical | No
23 |  |  |  |  | Please confirm the length of horizontal drilling required for railway line crossing. Also mark in proposed land layout. | Technical | Visit the site for these details
24 |  |  |  |  | Please confirm the length of the existing drains (on side of Gulf of Mannar and near the Bus stop end of the project) where existing slope is 20 degree. | Technical | It is recommended for the site survey to get the details.
25 |  |  |  |  | Any Big Tree/high voltage grid line going through the site? (Describe location, height of obstruction etc.) | Technical | No
26 |  |  |  |  | Any hill is there inside the land area? If yes then give description like approx. height and location i.e. in North/South/East/West | Technical | No
27 |  |  |  |  | Any hill/other-obstruction is there outside the plant boundary situated other than North side & capable of posing shadow in the land under discussion. Please give the approx. height and distance of such obstructions (hill/tower/tree etc.) from the plant boundary | Technical | the area is Shadow free and completely available for Solar PV plant
28 |  |  |  |  | Sanctioned Load | Technical | It is recommended for the site survey to get the details.
29 |  |  |  |  | Voltage Level | Technical | 22kV
30 |  |  |  |  | Installed Capacity of DG sets (if available) | Technical | It is recommended for the site survey to get the details.
31 |  |  |  |  | Installed Capacity & Voltage of Transformer | Technical | It is recommended for the site survey to get the details.
32 |  |  |  |  | Inverter Location from module | Technical | It is recommended for the site survey to get the details.
33 |  |  |  |  | HT / LT panel Location | Technical | It is recommended for the site survey to get the details.
34 |  |  |  |  | HT / LT panel rating | Technical | It is recommended for the site survey to get the details.
35 |  |  |  |  | Grid Level Voltage | Technical | 22kV
36 |  |  |  |  | Load operating voltage | Technical | 22kV
37 |  |  |  |  | Name and address of the Utility Company? Who is the contact person of the concerned Utility Company regarding inter-connectivity? | Technical | TANGEDCO, the contact details will be provided by VOC port.
38 |  |  |  |  | How far the utility grid line from the site and what is the kV rating of that line? Is it possible to inject power in this line? | Technical | It is recommended for the site survey to get the details.
39 |  |  |  |  | How many Grid substations are there with in a dia of 15-20 km? (Both existing and proposed) Give details of each substation as per the attached separate format. | Technical | It is recommended for the site survey to get the details.
40 |  |  |  |  | Whether the nearby substation has the excess capacity to take the power. If yes, how much in MW | Technical | It is recommended for the site survey to get the details.
41 |  |  |  |  | Any other solar plant is there nearby the proposed site? If yes give Company name, plant size. | Technical | at Indian Coast Guard quarters applicatory 2km
42 |  |  |  |  | Local / legal issue at site | Technical | No local/legal issue
43 |  |  |  |  | Nearest City | Technical | Tuticorin
44 |  |  |  |  | Local Transport available | Technical | yes
45 |  |  |  |  | Transporter details | Technical | The Tamil Nadu State Transport Corporation operates daily services
46 |  |  |  |  | Local warehouse availability | Technical | It is recommended for the site survey to get the details.
47 |  |  |  |  | Nearest bus stop | Technical | Thoothukudi New Bus Terminus in Kamarajar Salai.
48 |  |  |  |  | Nearest Rail station | Technical | Thoothukudi Railway Station
49 |  |  |  |  | Please provide the dimension of land as the dimension shown on layout are not readable. Also please provide the Topography survey in Auto Cad format with marking of land boundaries, trees, any transmission line or any other objets if available at site. | Technical | It is recommended for the site survey to get the details.
50 |  |  |  |  | Images of site and images of existing railway siding of SPIC Chemical factory from where 22 kV cable will pass. | Technical | Visit the site for these details
51 |  |  |  |  | Details and images of rout of underground cable and transmission line. | Technical | it will be provided as amednment
52 |  |  |  |  | Details of Substation, Bay availability, images of spare bay or space for Bay for Solar Plant connection at substation | Technical | 230/110/22kV Auto S/s, Muthaiapuram
53 |  |  |  |  | Coordinate of the Substation | Technical | Lat: 8.743434; Lon:78.146558
54 |  |  |  |  | Please also mention the type of land (Govt / Private) in transmission area. | Technical | Solar Plant location is with in VOCPT premises. The area from proposed Solar Power plant location up to the boundary of VOCPT is belongs to VOCPT. The area beyond VOCPT boundary and up to substation is under public/Private domain. Route map of transmission line is attached for reference