## Pre-Bid Queries
Tender for the Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 44 MW (AC) ground based Solar PV Power Plant at different sites including 10 years plant O&M at SCCL, Telangana, India
Tender No : SECI/C&P/PMC/11/0003/2021-22
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 | Annexure to Bid Data Sheet (BDS) : Qualifying Requirements (QR) | 3 of 7 | 1.2 | Route I IA. The bidder should have experience in EPC execution of Ground mounted Solar Projects on Turnkey basis including Design, Supply (Supply of Modules & Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), Installation and Commissioning of Grid connected Solar PV Power Plant of cumulative Capacity not less than 22 (Twenty Two) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. AND IB. Out of the above, the bidder should have experience in EPC execution of Ground mounted Solar Projects on Turnkey basis including Design, supply (Supply of Modules & Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), installation & commissioning of at least 02 (Two) Grid connected Solar PV Power Plant Projects having an individual capacity of 5 (Five) MW or above in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. | We have two separate order i.e. (1) 225MWp DC BOS & (2) 300MW AC BOS from the same Customer for the same project. LOA copies and respective Commissioning Certificates are attached herewith for your kind information please. We would like to inform you that customer had issued separate orders due to their execution methodology. We request you to consider separate orders of DC BOS Package and AC BOS Package against the tender requirement i.e. “EPC execution of Ground mounted Solar Projects on Turnkey basis” and allow us to bid for the tender. | Technical | Accepted
2 | Section-VII - B - Electrical - 1 - Photovolatic Module | 25 | 1.3.2 | The Employer reserves the right to conduct Pressure Cooker (PC) test/ Highly Accelerated Stress Test (HAST) to confirm the durability of the back sheet in accelerated conditions. | No facility to conduct the test in factory, but the test report can be provided performed by the supplier per lot basis. Please Confirm | Technical | Accepted
3 | Section-VII - B - Electrical - 1 - Photovolatic Module | 26 | 1.3.7 | Each PV Module shall be provided a RFID tag which is embedded inside the module lamination and must be able to withstand harsh environmental conditions. | As per MNRE, RFID can be embedded inside or outside of the module. VSL will paste RFID outside of the module behind the back-label. Please Confirm | Technical | Terms and Conditions of the tender prevail
4 | Section-VII - B - Electrical - 1 - Photovolatic Module | 26 | 1.3.7.iii | Type of cell: Mono / Multi | Not mentioned on the RFID separately, but it can be identified from module model name. Please Confirm | Technical | Accepted
5 | Section-VII - B - Electrical - 1 - Photovolatic Module | 27 | 1.4.2 | The modules shall be warranted for minimum of 10 years against all material/ manufacturing defects and workmanship. | Workmanship is not uder module supplier's scope. Please Confirm | Technical | Terms and Conditions of the tender prevail
6 | Section-VII - B - Electrical - 1 - Photovolatic Module | 25 | 1.2 | 1.2 - Technical requirments Origin of PV Modules Cells and modules shall be domestically manufactured. | Can we consider cell outside india. Please Confirm. | Technical | Terms and Conditions of the tender prevail
7 | Section-VII - 4 Procurement & Supply | 8 | 4.1.20 | CCTV cameras for plant surveillance | Please clarify the surveillance area so we can easily plan and calculate the CCTV camera Nos.. | Technical | Shall be determined during detailed engineering as per the relevant clause in the Technical Specifications
8 | Section-VII - 3 -Solar DC Cable | 30 | 3.3 | DC cables shall be single core, armoured, Flame Retardant Low smoke (FRLS), PVC outer sheath conforming to IS 7098-II. DC cable with positive polarity should have marking of red line on black outer sheath. | Cable shall be provided FR type sicnce cable directly buried. Please Confirm | Technical | Terms and Conditions of the tender prevail
9 | Section-VII - 7 -AC Cable | 53 | 7.2 | 7.2 All AC cables shall be flame retardant, low smoke (FRLS) type designed to withstand all mechanical, electrical and thermal stresses develop under steady state and transient operating conditions. | Cable shall be provided FR type sicnce cable directly buried. Please Confirm | Technical | Terms and Conditions of the tender prevail
10 | Section-VII - 23 -CCTV Camera | 119 | 23.1 | ii. Along the Plant Perimeter: Covering complete perimeter of Plant Area to capture all possible intrusion | As Since peripheral fencing will covered the plant perimeter. Bidder propose to provide CCTV at stragies location such as main gate, Control building, ICR and avoid CCTV from plant perimeter. Please Confirm | Technical | Terms and Conditions of the tender prevail
11 | Functional Guarantees | 292 | ANNEXURE 2 | C. Capacity Utilization Factor (CUF) for Solar Plant shall be calculated as per the following formula. | Formula not mentioned in said tender. | Technical | Please refer S. No. 30 of Amendment
12 | Section-VII - 2 - SCB | 29 | 2.2.6 | Resistance Temperature Detector (RTD) type or semiconductor type temperature sensor shall be provided to monitor the cabinet temperature. | As this SCB is not having any monitoring features, this RTD sensor is not applicable. | Technical | The Clause is deleted. Please refer S. No. of Amendment
13 | Section-VII - 6.4 Circuit Breakers | 45 | 6.4.3 | The rated control voltage of the spring charging motor shall be 110 VDC/230 VAC. Closing coil shall operate at all values of voltages between 85% and 110% of rated voltage. | Please clarify what is control supply required for closing & trip coils along with the meters and relays etc, for inverter station locations we propose to have 230V UPS supply and for Main pooling HT panel we propose to mention 110V DC / 220V DC | Technical | Terms and Conditions of the tender prevail
14 | Section-VII - 617.14.1.2 Special Tests | 89 | 17.14.1.2 | Special Tests: (i) Short circuit withstand test as per IS 2026-5/IEC 60076-5 | As these transformer ratings are non standard in nature and not readily available with all suppliers , we request SECI to accept the IEC-60076 short circuit similarity comparison as per annexure A & B as all PSU accept the same. | Technical | Acceped
15 | Section-VII - Annexure- D - MANDATORY SPARES | 222 | 3 | String Monitoring Unit 1% of total supply SMU Communication Card 1% of Total supply | As per technical specifications no string monitoring features required, hence in spare list same shall not be applicable, please correct the same. | Technical | Please refer S. No. 28 of Amendment 1
16 | Section-VII - 2 - SCB | 29 | 2.2.2 | One spare input terminal along with connector shall be provided for each SCB. | One spare shall be provided in String combiner box. But the cable sizing shall be performed as per actual load current. Spare feeder current shall not to be considered the Cable sizing. Kindly Accept. | Technical | Accepted
17 | Section-VII - 3 - Solar and DC cable | 30 | 3.5 | In case of central inverters, average voltage drop in the cables (from PV Modules to PCU) shall be limited to 1.5 % of the rated voltage | Bidder requests SECI to increase the average voltage drop to 2% from PV Modules to PCU. Kindly Accept. | Technical | Terms and Conditions of the tender prevail
18 | Section-VII - 4 - PCU | 34 | 4.4.11 | String inverter, if installed in open, shall be placed inside a canopy shed with at least 15 cm in all directions. | As enclosure protection class is IP 65 or better, Bidder requests SECI to remove the requirement of canopy shed if it is installed in open. Kindly accept. | Technical | Terms and Conditions of the tender prevail
19 | Section-VII - 6 - Battery Energy Storage System | 249 | 6 | 6 Battery Energy Storage System | Battery Energy storage system is not there in the tender scope of work. Whether it is place by mistakenly. Kindly clarify. | Technical | The Clause does not apply to this tender.
20 | Section-VII - 18 - Nitrogen Injection Fire Protection System | 90 | 18 | Nitrogen Injection Fire Protection System | Bidder understands that only NIFPES shall be considered for power transformer. HVWS system for the shall not be required. Kindly confirm. | Technical | NIFPS shall be applicable for the transformer as per the CEA guidelines
21 | Section-VII - 19 - Control and Relay Panel | 94 | 19 | Control and Relay Panel | As there is no specific requirement mentioned for protection requirement of line feeder & other feeders, we understand that same shall be considered inline with CEA guidelines. Please confirm. | Technical | Accepted
22 | Section-VII - 20.5 - Disconnector | 103 | 20.5.1 | Rated peak withstand current for isolator & earth switch 80 kAp | As per referred clause, it is mentioned as "Rated short time dynamic rating 80kA" However, as per IEC/IS for STC of 31.5kA Dynamic Short Circuit rating shall be 78.75 (The value of the rated dynamic current (Idyn) shall normally be 2.5 times the rated short-time thermal current (Ith)) . Further, we shall be considered STC as 31.5kA for proposed 132kV System and Rated short time dynamic rating shall be considered inline with IEC. Please confirm. | Technical | Terms and Conditions of the tender prevail
23 | Section-VII - 21.3 - Lighting Levels | 114 | 21.3.4 | Plant boundary/ Peripheral area shall be illuminated with chain-link/Boundary wall post mounted LED floodlights (at every 100m) for area lighting | Street light proposed instead of floodlightswith avg. 5 lux. Please Confirm | Technical | Terms and Conditions of the tender prevail
24 | Section-VII - Functional Guarantees | 292 | ANNEXURE 2 | Eac is the number of units recorded in the plant end ABT meter excluding auxiliary consumption, kWh | Bidder understand that generation gurentee is provided in the plant end only (excluding transmission loss in between plant to TSTRANSCO / SCCL Sub station ) | Technical | Terms and Conditions of the tender prevail
25 | Section-VII - 1 - Project Particulars | 3 | Project Particulars | 9000 m** **It includes strengthening of 5000 m 33 kV existing line from plant location to Burli Pit switch station & 4000 m new 33 kV line from Burli Pit switch station to connecting substation. | For 5000 m existing 33 KV extension line please clarify the below points.. 1. Transmission line route 2. Please clarify, If any modification required or not. If yes, than in scope of bidder or owners along with O&M. 3. Please confirm, if any fault or shutdown happen due to fault is existing line, than the generation guarentee shall be modified. 4. Bidder understand that, Shut down approval & charges to be the existing TL shall be borne by client. | Projects | 1) Transmission line route survey is in the scope of bidder 2) All the required modification works ( if any ) including O&M are in the scope of bidder 3) Terms & conditions of NIT prevails 4) Shutdown charges / approval is not applicable for this existing 5000m 33KV Transmission line. No shutdown charges are required.
26 | Section-VII - 9 - LT Switchgear | 55 | 9.2 | Operating Duty O – 3min – CO – 3min – CO | Operating Duty O – 0.3 min - CO - 3 min Please Clarify | Technical | Please refer S. No. 6 of Amendment
27 |  |  |  | General | Please share the coordinates or live location of proposed land or sub station where we can evacuate the power supply. | Projects | Bidder should obtain these details on his own, during site visit.
28 |  | 177 |  | General (Land / Boundary coordinates) | Chennur-2 Incline Boundary coordinates is wrong, when I placed in google earth I found that the location is outside india. Please recheck and confirm. | Projects | Boundary coordinates are provided as per the available data. However, bidder can verify during their site visit.
29 | C Civil, Mechanical and Plumbing Works | 128 | 3.3 | The field investigations shall mainly include drilling of min. 5 m deep BHs, The BH near MCR and ICR shall be 10m deep. | Foundation depth of structures shall be well within 5 m depth. So boreholes of 10 m depth will not be required. Please confirm the same. | Technical | boreholes of 10 m depth are required near the ICR, MCR. Terms and Conditions of the tender prevail
30 | C Civil, Mechanical and Plumbing Works | 128 | 3.3 | There shall be minimum 1 nos. of BH per 10 acres of the area. In case the project plot is divided in to number of discrete blocks separated from each other, min. 3 nos. of bore holes, 2 trial pits, 2 ERT and 2 CBR tests shall be taken per such block with at least 1 No. of BHs per 5 acres. | Provision of boreholes at each 10 acre will increse the timeline for soil investigation report. So it is proposed to consider one borehole per 12.5 acre of Land area. | Technical | Terms and Conditions of the tender prevail
31 | C Civil, Mechanical and Plumbing Works | 132 | 5.4 | The contractor is responsible for making the site ready and easily approachable by clearing bushes, felling of trees (mandatory permissions/ licenses/ statutory clearances from competent authorities if required for cutting of trees, blasting or mining operations, disposal of waste material etc. shall be obtained by the contractor), | Cutting & removal of big trees (if any) and relevant permissions shall be in client scope. Removal of bushes, shurbs etc shall be in bidders scope. Please confirm the same. | Technical | Terms and Conditions of the tender prevail
32 | C Civil, Mechanical and Plumbing Works | 132 | 5.4 | Except in exceptional cases (with approval of the Engineer), filling shall be made up of cohesive non-swelling material. | Backfilling shall be done with excavated soil with proper compaction. Please confirm the same. | Technical | Terms and Conditions of the tender prevail
33 | 6 Roads | 133 | 6.2 | The Approach road connecting nearest public road and the Main gate shall be of 4.0m wide carriage way with 0.5m wide shoulders on either side. | Please confirm length of approach road to be constructed for each site. | Projects | The length of approach road can be finalised only after detailed engineering / approved plant layout.
34 | 6 Roads | 134 | 6.3 | However, following minimum road section details shall be followed: vi. Gravel Shoulders conforming to Cl 407 of MORD specs: 150mm compacted thick, compacted to 100 % of max. dry density | It is proposed as per following: vi. Gravel Shoulders conforming to Cl 407 of MORD specs: 100mm compacted thick, compacted to 100 % of max. dry density. Please confirm. | Technical | Terms and Conditions of the tender prevail
35 | 6 Roads | 134 | 6.3 | iv. Granular/ gravel sub-base course (CBR>20%), conforming to Cl. 401 of MORD specs: 175 mm compacted thick, compacted to 100% of max dry density | It is proposed as per following: iv. Granular Subbase, compacted 150mm thick granular sub-base (Gr-I) compacted to 100% of max dry density. Please confirm. | Technical | Terms and Conditions of the tender prevail
36 | 6 Roads | 134 | 6.4 | When the subgrade is silty or clayey soil and the annual rainfall of the area is more than 1000 mm, a drainage layer of 100 mm over the entire formation width should be provided conforming to the gradation given in Chapter 6 of IRC SP-20. This layer will form a part of the designed thickness of sub-base. | In that scenaio, subgrade shall be treated & compacted accordigly to increase CBR > 2%. Please confirm the same. | Technical | Terms and Conditions of the tender prevail
37 | 6 Roads | 135 | 6.7 | The water supply pipe for module cleaning and service/ drinking water shall be routed through Medium class GI steel pipe of required dia. conforming to IS: 1161. | Please consider HDPE (IS: 4984) or PVC (IS:4985) pipe for module cleaning service and drinking water as it is rust free and easy to install. | Technical | Please refer Cl 35(Module Cleaning System Specs) of Sub Section C of Sub Section VII-C(Technical Specifications) of NIT.of The said clause in query is intended for routing the water supply pipe at locations of crossings. Terms and conditions of Tender prevail.
38 | 6 Roads | 135 | 6.8 | Minimum dia. of casing pipe to be used at any facility like electric cable, water pipe line etc. shall be 150mm. | 150 mm dia is not required for water pipe line please consider 50 mm & 32 MM dia for water pipe line i.e. standard practice | Technical | Please refer Cl 35(Module Cleaning System Specs) of Sub Section C of Sub Section VII-C(Technical Specifications) of NIT.of The said clause in query is intended for routing the water supply pipe at locations of crossings. Terms and conditions of Tender prevail.
39 | 6 Roads | 135 | 6.1 | There shall be no peripheral road. However, about 2.5m wide corridor compacted to a depth of 300mm shall be left along inside of the plant boundary suitably maintained clean of any vegetation and shall be provided with adequate illumination for movement of security personnel. Any undulations shall be made good with locally available coarse grained material to have fairly level passage way. | Please allow 2.5m wide corridor compacted to a depth of 200mm. Please confirm the same. | Technical | Terms and Conditions of the tender prevail
40 | 7 Surface/ Area drainage | 137 | 7.14 | the Contractor shall explore provisions for rain water harvesting system for water conservation by constructing suitable collection wells along the drains or through provision of detention ponds or percolation/recharge pit etc. at major drainage outfalls. | In case there are no outfall point for discharging strom water, then only recharge pit will be provided. Please confirm the same. | Technical | Terms and Conditions of the tender prevail
41 | 10 Design Loads | 139 | 10.10.2 | For estimation of design wind loads on purlins (Table 8 of IS 875- Part 3), WL (downward) and WL (upward) on modules (laid in the profile of mono slope canopy) shall be applied such that the center of pressure should be at (0.3 × length of canopy) from windward end (for simplicity, the wind load distribution may be taken as triangular with max. value at windward end). Solidity ratio (∅) shall be taken as 0.0. | The traingular load consideration shall be applied only in exterior 2 tables along all periphery. For other interior tables, uniformly distributed load will be applied. Please confirm the same. | Technical | Terms and Conditions of the tender prevail
42 | 13 Module Mounting Structure (MMS) | 147 | 13.23 | Two numbers of anti-theft fasteners of stainless steel on two diagonally opposite corners for each module shall be provided. | Anti theft fasterners will obstruct the easy replacement of defected modules with new one. Please confirm. | Technical | Terms and Conditions of the tender prevail
43 | 13 Module Mounting Structure (MMS) | 148 | 13.33 | The length of one unit (Table) of MMS shall not generally be more than 20m. | For 1500V system, table length will be 30m for 2PX30 table size. Please allow the same. | Technical | Accepted
44 | 13 Module Mounting Structure (MMS) | 148 | 13.36 | The length of any cold formed section (CFS) shall not be more than 5.5 m. | For purlin, please allow length upto 6.0 m. | Technical | Terms and Conditions of the tender prevail
45 | 19 Roofing | 154 | 19.2 | The water proofing treatment shall be in situ five course water proofing treatment with APP (Atactic Polypropylene) modified Polymeric membrane over roof consisting of first coat of bitumen primer @ 0.40Kg per sqm, 2nd & 4th courses of bonding material @ 1.20 kg/sqm, which shall consist of blown type bitumen of grade 85/25 conforming to IS : 702, 3rd layer of roofing membrane APP modified Polymeric membrane 2.0 mm thick of 3.00 Kg/sqm weight consisting of five layers prefabricated with centre core as 100 micron HMHDPE film sandwiched on both sides with polymeric mix and the polymeric mix is protected on both sides with 20 micron HMHDPE film. The top most layer (5th layer) shall be finished with brick tiles of class designation 10 grouted with cement mortar 1:3 (1 cement: 3 fine sand) mixed with 2% integral water proofing compound by weight of cement over a 12 mm layer of cement mortar 1:3 (1 cement: 3 fine sand) and finished neat. | Instead of five layer water proofing, simple bitumen felt water proofing will be provided. Please confirm the same. | Technical | Terms and Conditions of the tender prevail
46 | 35 PV Module Cleaning System | 161 | 35 | PV Module Cleaning System – Wet or Dry Type | Module Cleaning System will be provided as Wet Cleaning System with Water. | Technical | Both wet and Dry type Module Cleaning Systems are acceptable. Terms and Conditions of the tender prevail
47 | 35 PV Module Cleaning System | 162 | 35.6 | The module cleaning system shall include construction of RCC tank or supply and installation of Ground mounted PVC tank (s) of required storage capacity. | Module Cleaning System water tanks will be Ground mounted PVC tanks of required storage capacity. Please consider the same. | Technical | Acceptable as per the Clause
48 | 35 PV Module Cleaning System | 162 | 35.1 | Module cleaning procedure and pressure requirement at discharge point shall be as per the recommendation of PV module manufacturer. However, discharge pressure at outlet shall not be less than 50kg/cm2 (5 MPa) | As per stand ard practice 2.5 to 5 Kg/cm2 (2.5-5 bar) pressure considered at outlet. Please confirm the pressureat cleaning point. | Technical | Please refer S. No. 27 of Amendment
49 | SECTION - VII | 8 | 4.1.24 | Design & construction of Transmission line/ cable at required voltage level from plant take off point to the designated substation including right of way (ROW) and construction of bay at designated substation as per DISCOM/TRANSCO requirements/procedures. | ROW for 22 km at 132 KV & 18 km 33 kV transmission line for the three porposed solar plant shall in client's scope. Please share the location / cooridnates for the respective substaion where the power shall be evacauted. | Technical | Terms and Conditions of the tender prevail
50 | 6 Roads | 133 | 6.2 | The top of road (TOR) elevation shall be minimum 200 mm above FGL to avoid flooding of roads during rains. | It is proposed that top of road (TOR) elevation shall be minimum 150 mm above FGL to avoid flooding of roads during rains. The crown of the road shall be minimum 150 mm above FGL.. Please confirm. | Technical | Terms and Conditions of the tender prevail
51 | BID VALIDITY | 63 | BDS/8 | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of o penning of Techno Commercial Bid (Envelope-I) | Considering the volatility on the market Bid Validity should be upto 90 days from the date of opening of Techno Commercial Bid (Envelope-I) | Contractual | The terms and conditions of the tender document shall prevail.
52 | GCC | 83 | 1.1.32 | EFFECTIVE DATE means the date of issuance of Notification of Award/ Letter of Intent/ Letter of Award (LOA) from which the Time for Completion shall be determined or any other specific date as provided in the Notice to Proceed (NTP), in case the NTP is applicable. | Effective date to be considered from issuance of NOA/LOA or hand over of clear embumbrance free workable land along with sub-station whichever occurs later | Contractual | The terms and conditions of the tender document shall prevail.
53 | SCC | 155 | 3 | The Time for Commissioning for the cumulative capacity of 44 MW Solar PV Power Plant at 03 different sites along with other associated equipment as per this tender document in total shall be 12 (Twelve) Months from the Date of the Notification of Award NOA/LOA /LOI | Considering the exhaustive scope of work including Transmission Line and three different locations , time of commissioning should be 18 months from the 'effective date' | Projects | All three Projects sites have different scope of work and contractor shall have to work at all three location simultaneously and shall have to commission the cummulative capacity of 44 MW within 12 (Twelve) Months from the Date of the Notification of Award NOA/LOA /LOI
54 | SCC | 157 | 4 | Cutting of trees, bushes and vegetation from site (including permission from local authorities) and disposal thereof. The site should be maintained in vegetation free condition during erection stage (at any point of time) i.e., up to start of O&M Contract | Tree cutting , relocation of Overhead Transmission line , removal of any existing structure will be under Client's scope | Projects | Tree cutting, relocation of Overhead Transmission line , removal of any existing structure will be under Contractor's scope
55 | SCC | 162 | 19 | Interest bearing initial advance (OPTIONAL) of 10% of the Contract Value (i.e., total sum of all the Supply Contract) shall be released to the contractor upon receipt of unconditional acceptance of NOA, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final commissioning total amounting to 110% of total advance amount | Please allow interest free advance | Contractual | The terms and conditions of the tender document shall prevail.
56 | NIT | 6 |  | EMD CAN BE SUBMITTED BY THE BIDDERS JOINTLY FOR THE COMPLETE 44 MW PROJECT CAPACITY. HOWEVER, THE SUCCESSFUL BIDDER WILL BE REQUIRED TO SUBMIT RESPECTIVE SEPARATE CONTRACT PERFORMANCE SECURITIES & ADVANCE BANK GUARANTEES (IF AVAILED) FOR INDIVIDUAL SITES AS THERE WILL BE INDIVIDUAL CONTRACT AGREEMENTS WITH THE SUCCESSFUL BIDDER BASED ON SITE CAPACITY. OWNER RESERVES THE OPTION TO REDUCE ANY OF THE ABOVE-MENTIONED SITE CAPACITY FROM THE OVERALL CUMULATIVE CAPACITY BEFORE/AFTER AWARD OF CONTRACT AGREEMENT. ACCORDINGLY, THE TOTAL PROJECT PRICE WILL BE PROPORTIONATELY REDUCED & THE FINAL PROJECT PRICE ARRIVED AS SUCH AFTER REDUCTION WILL BE THE FINAL PROJECT PRICE OF THE CONTRACT AGREEMENT. | We would request you to withdraw this clause as quoted prices are having viability for 44 MW Capacity. Any reduction in awarded MW Capacity shall entitle bidder to withdraw its offer | Contractual | The terms and conditions of the tender document shall prevail.
57 | NIT | 7 | 2 | Singareni Collieries Company Limited (SCCL), envisages the execution of Green Energy by way of implementing Solar PV Power Plant at SCCL in the State of Telangana. This would not only be a leap towards the use of Green Energy for SCCL but also be means of selfreliant and Economical Energy which would capitalize the abundance of Solar Energy. | Pls confirm if this project is a captive project for SCCL or SCCL has a PPA with Discom for selling in market. | Projects | It is a Captive Project
58 | GCC | 82 | 1.1.19 | CONTRACT PRICE/CONTRACT VALUE/PROJECT VALUE means the firm value of the final quoted price, as a result of e- RA (if applicable), by the successful bidder specified in its financial proposal as the sum of individual contract value of Supply & Services (Supply of goods, F&I, Design, installation, Civil Works etc) as mentioned under the different work heads specified in the financial proposal including all the applicable taxes/ Goods & Service taxes | Pls confirm if the Contract value includes O&M as well? | Contractual | Pl refer to the definitions section under GCC for more clarity on Contract value.
59 | GCC | 84 | 1.1.48 | NTP means Notice to Proceed subsequent to the placement of LOA/NOA/LOI. NTP will be issued by the owner within a maximum time frame of 90 days from the date of LOA/NOA/LOI, failing which the LOA/NOA/LO shall stand withdrawn without creating any further liability on either party. In such case EMD/PBG, as applicable submitted by the contractor shall be released | In view of extremely volatile market prices, we have to commence project execution for timely PO placement/ordering. Henc epls restrict the NTP issuance to within 15 days. | Contractual | The terms and conditions of the tender document shall prevail.
60 | GCC | 96 | 20 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities | We understand that the delay LD is not applicable on O&M portion of contract. Pls confirm. | Contractual | O&M contract is a separte contract with different LD conditions.
61 | GCC | 119 | 53.3 | Wherever references are made in the Contract to codes and standards in accordance with which the Contract shall be executed, the edition or the revised version of such codes and standards current at the date of bid submission shall apply unless otherwise specified. | We understand that Change in Codes & Standards during execution is a part of Change in Law | Technical | Bidder has to carryout the works as per the prevailing ( as on date of execution) codes & regulations of statutory authorities.No extra charges will be paid on this account.
62 | GCC | 127 | 70 | Suspension of Works 70.1 i) Subject to the provisions of sub-para (ii) of this clause, the Contractor shall, if ordered in writing by the Engineer-in-Charge/Project Manager, or his representative, temporarily suspend the Works or any part thereof for such written order, proceed with the Work therein ordered to be suspended until, he shall have received a written order to proceed therewith. The Contractor shall not be entitled to claim compensation for any loss or damage sustained by him by reason of temporary suspension of the Works aforesaid. However, suitable time extension may be considered at the sole discretion of the owner. ii) In case of suspensions of entire Work, ordered in writing by Engineer-in Charge/ Project Manager, for a period of more than 03 (Three) months, the Contractor shall have the option to terminate the Contract. | We would request owner to kindly compensate for costs incidental to such suspension of works. Given the fixed price nature of this tender, such 3 months suspension without financial compensation shall cause a a serious loss to the Contractor. | Contractual | The terms and conditions of the tender document shall prevail.
63 | GCC | 148 |  | Above mentioned Arbitration clause will be applicable for the Disputes where the amount of claim is less than or equal to INR 1Crore (Indian Rupees One Crore only). For the cases of disputes where the amount of claim is more than INR 1 Crore (Indian Rupees One Crore), such disputes will be settled through commercial Courts established under the Commercial Courts, Commercial Division and Commercial Appellate divisions of High Courts act, 2015 | We would request to enhance the ceiling amount from INR 1 crs to 25 crs | Contractual | The terms and conditions of the tender document shall prevail.
64 | SCC | 155 | 1 | 1.1.49 Operational Acceptance means completion of all the required works / activities to achieve the rated generation and successful demonstration of Guaranteed PR for 30 days. | We understand that 30 days stated herein is the aggregate of 30 days. | Technical | Accepted
65 | SCC | 156 | 3.1 | Operational Acceptance of plant D + 15 Months | Project milestone schedule listed under clauses 3.1 onwards needs to be reviewed for correctness | Technical | The terms and conditions of tender document will prevail
66 | SCC | 158 | 10 | 20.1.1 For delay in synchronization & commissioning:INR 20,000/MW/day for the capacity not commissioned. On this account the maximum applicable LD is 3% of total contract price | For the purpose of delay LD ceiling ,we understand that the total contract price excludes O&M portion. Pls confirm | Contractual | Yes
67 | SCC | 160 | 11 | First Stage (Supply and Services): The value of the Contract Performance Security shall be 4% (four percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 135 Months (12 Months Project commissioning period) + prescribed O & M Period, i.e., 120 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of one year and the same may be extended every year till completion of the total 135 months period | 1.Pls reduce the CPBG to 3% 2.Pls confirm if the O&M portion of contract is included for furnishing CPBG? | Contractual | 1. Pl refer Amendment 1 for the same. 2. No
68 | SCC | 161 | 15 | Replace the existing clause by following: In the matter of connectivity of Plant to DISCOM’s substation, the Owner will take the necessary connectivity permission, however, all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc. are to be taken by the Contractor. All the required fees including statutory fees, Supervision charges etc. shall be paid / born by the contractor. | 1.Since site selection and substation selection is by owner therefore request you to kindly consider ROW in your scope.This will enable timely completion. 2. Since connectivity approval is by SECI therfore Bay allocation related charges shall also be borne by SECI | Projects | The terms and conditions of tender document will prevail
69 | SCC | 161 | 15 | Replace the existing clause by following: In the matter of connectivity of Plant to DISCOM’s substation, the Owner will take the necessary connectivity permission, however, all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc. are to be taken by the Contractor. All the required fees including statutory fees, Supervision charges etc. shall be paid / born by the contractor. | Pls confirm if the receiving bays at DISCOM's substation shall be constructed by DISCOM or SECI? | Projects | The receiving bays at DISCOM's substation shall be constructed by the contractor only.
70 | TS | 8 | 4.1.25 | Any re-arrangement/ replacement of substation equipment/ materials, including bay construction, if required, at the evacuating substation necessary for evacuation of power from the Plant. | Pls clarify the objective of re arrangement /replacement of evacuation substation | Projects | The terms and conditions of tender document will prevail
71 | TS | 10 |  | All other approval as and when, as necessary for setting up of a solar power plant including CEIG/ CEA, connectivity, power evacuation, railways, PTCC power line crossing, panchayat, NHAI etc. as per the suggested guidelines | As per SCC ,connectivity is in SECI's scope. Pls confirm. | Technical | connectivity is in SECI's scope
72 | TS | 11 |  | All statutory approvals/permissions and/or No Objection Certificates (NoC) etc. from the DISCOM for obtaining connectivity at the substation as per Project Particulars provided above |  | Projects
73 | TS | 221 | Annexure C | Liquidated Damages for Shortfall in PR For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service and absolute value of O & M Contract) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance. Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made. | 1)We would request you to release the payments against OAT. Contractor's liability on a/c of shortfall in OAT is aggregated to 10%+5% +5% i.e. 20% , which is extremely. | Technical | Terms and Conditions of the tender prevail
74 | TS | 221 | Annexure C | Liquidated Damages for Shortfall in PR For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service and absolute value of O & M Contract) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance. Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made. | 1) We understand that O&M value is excluded from PR test related LD. | Technical | Please refer S.31 No. of Amendment
75 | IFB | 12 |  | EMD Amount: INR 5,12,00,000 (Indian Rupees Five crores and twelve lakhs only). | Request to share the below mentioned bank details for BG processing 1.Bank Name 2.Branch Name 3.IFSC Code | Contractual | Pl refer "Financials" section on SECI's website @ www.seci.co.in for the same
76 |  |  |  | EMD | Request to wave off the EMD amount as per the present Govt rules | Contractual | The terms and conditions of the tender document shall prevail.
77 |  |  |  | For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service and absolute value of O & M Contract) shall be levied. | We understand that the contract value is supply + service value not O&M value. As O&M will start on the after the successful OAT. Please confirm | Technical | Please refer S. 31 No. of Amendment
78 |  |  |  |  | Please provide the details scope of work for strengthening of 5km existing transmission line | Projects | Bidder has to assess the scope during site visit. Also, necessary line clearances should be maintained as per TSNPDCL guidelines. However, SCCL will assist the bidder during site visit.
79 |  | 33 | Section- VII_4_PCU | Degree of protection : Central Inverter – IP 20 (Indoor)/IP 54 (Outdoor), String Inverter – IP 65 | We can design AC system (PCU) as per combination of both inverter (Central + String). Please confirm | Technical | Accepted

## Ammendment-1
Tender No : SECI/C&P/PMC/11/0003/2021-22
Tender for the Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 44 MW (AC) ground based Solar PV Power Plant at different sites including 10 years plant O&M at SCCL, Telangana, India
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | Section-V Special Conditions of Contract | 7 of 13 | 11 | Replace the existing clause by following: The Contract Performance Security shall be in the form of Bank Guarantee only and shall be in the currency of the Contract and will be issued individually for all the sites (Site 1,2 & 3) in the name of the Owner as “Singareni Collieries Company Limited, Telangana, Kothagudem, Telangana State” The Contract Performance Security against this Contract need to be furnished as mentioned below: 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 4% (four percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 135 Months (12 Months Project commissioning period) + prescribed O & M Period, i.e., 120 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of one year and the same may be extended every year till completion of the total 135 months period. | Replace the existing clause by following: The Contract Performance Security shall be in the form of Bank Guarantee only and shall be in the currency of the Contract and will be issued individually for all the sites (Site 1,2 & 3) in the name of the Owner as “Singareni Collieries Company Limited, Telangana, Kothagudem, Telangana State” The Contract Performance Security against this Contract need to be furnished as mentioned below: 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 3% (three percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 138 Months (15 Months Project commissioning period) + prescribed O & M Period, i.e., 120 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of one year and the same may be extended every year till completion of the total 138 months period.
2 | Technical Specification | 13 of 154 | 2.2.6 | Resistance Temperature Detector (RTD) type or semiconductor type temperature sensor shall be provided to monitor the cabinet temperature. | Void.
3 | Technical Specification | 18 of 154 | 4.4.11 | AC combiner box for string inverter configuration shall comply with Clause 9 of the Technical Specifications with exception of rated system voltage. | AC combiner box for string inverter configuration shall comply with Clause 9 of the Technical Specifications with exception of the following: i) Rated System Voltage- as per the inverter output voltage. ii) IP Rating - IP55 iii) Metering system - Not required
4 | Technical Specification | 32 of 154 | 6.5.14 | The numerical relay shall have RS-232/RS-485/RJ-45/USB ports on front side for local communication with PC and on rear side for remote communication to SCADA system | The numerical relays and meters at 33kV and above voltage level shall be IEC 61850 compliant for communicating with the SCADA system.
5 | Technical Specification | 38 of 154 | 7.8.2 | Cables within transformer yard and switchyard shall be laid through RCC cable trench with supports. | Cables within the main (plant end) switchyard shall be laid through RCC cable trench with supports.
6 | Technical Specification | 39 of 154 | 9.2 | Air Circuit Breaker (ACB) Type Air-break Rated Current As per system requirement Operating Duty O – 3min – CO – 3min – CO | Air Circuit Breaker (ACB) Type Air-break Rated Current As per system requirement
7 | Technical Specification | 54 of 154 | 13.1 | Lightning Protection System (LPS) for entire plant against direct lighting strokes shall be provided as per IEC 62305:2010 or NFC 17-102:2011. | Lightning Protection System (LPS) for entire plant against direct lighting strokes shall be provided as per IEC 62305:2010 or NBC.
8 | Technical Specification | 54 of 154 | 13.8 | Type test reports as per IEC 62305:2010 or NFC 17-102:2011 shall be submitted during detailed engineering for approval. | Type test reports as per IEC 62305:2010 shall be submitted during detailed engineering for approval.
9 | Technical Specification | 54 of 154 | 13.4 and 13.5 | Lightning Protection System | Void.
10 | Technical Specification | 56 of 154 | 15.1.3. iv) | The interface shall allow integration with Surveillance System(s), Module Cleaning System and various other O&M support systems to provide a Data Analysis and Decision Support System for smooth and efficient Plant Operations. | The interface shall allow integration with Module Cleaning System and various other O&M support systems to provide a Data Analysis and Decision Support System for smooth and efficient Plant Operations.
11 | Technical Specification | 59 of 154 | 15.4.6 | The SCADA system shall enable integration with other sub-systems at the plant for supporting O&M activities. The list shall include but not limited to: (i) Surveillance Cameras, (ii) Module Cleaning System – For monitoring of water usage and efficacy of cleaning process (in case of Wet Type Cleaning System). | The SCADA system shall enable integration with other sub-systems at the plant for supporting O&M activities. The list shall include but not limited to: (i) Module Cleaning System – For monitoring of water usage and efficacy of cleaning process (in case of Wet Type Cleaning System).
12 | Technical Specification | 62 of 154 | 15.9.2 | Operating System - Operating System and Database shall be of enterprise scale (RedHat Linux or equivalent Linux OS, Oracle/MySQL or equivalent DB), with required AMC for 5 years. | Operating System - Operating System and Database shall be of enterprise scale (RedHat Linux or equivalent Linux OS, Oracle/MySQL or Windows or equivalent DB), with required AMC for 5 years.
13 | Technical Specification | 79 of 154 | 19.3.2 | Auxiliary voltage of the relays shall be 110 VDC and the relays shall be capable of operating continuously between 80 – 120% of auxiliary voltage. | Relays shall operate on suitable DC auxiliary voltage and the relays shall be capable of operating continuously between 80 – 120% of auxiliary voltage.
14 | Technical Specification | 11 of 154 | 1.4.2 | The modules shall be warranted for minimum of 10 years against all material/ manufacturing defects and workmanship. | The modules shall be warranted against all material/ manufacturing defects and workmanship for minimum of 10 (ten) years from the date of supply.
15 | Technical Specification | 20 of 154 | 4.8 | The complete Power Conditioning Unit shall be warranted against all material/ manufacturing defects and workmanship for minimum of 5 (five) years. | The complete Power Conditioning Unit shall be warranted against all material/ manufacturing defects and workmanship for minimum of 5 (five) years from the date of supply.
16 | Technical Specification | 37 of 154 | 7.6 | All cables shall be warranted for minimum of 1 (one) year against all material/ manufacturing defects and workmanship. | All cables shall be warranted for minimum of 1 (one) year against all material/ manufacturing defects and workmanship from the date of supply.
17 | Technical Specification | 50 of 154 | 11.6 | Batteries and battery charger shall be warranted for minimum of 2 (two) years against all material/ manufacturing defects and workmanship. | Batteries and battery charger shall be warranted for minimum of 2 (two) years against all material/ manufacturing defects and workmanship from the date of supply.
18 | Technical Specification | 73 of 154 | 17.13 | The power transformer shall be warranted for minimum of 5 (five) years against all material/ manufacturing defects and workmanship. | The power transformer shall be warranted for minimum of 5 (five) years against all material/ manufacturing defects and workmanship from the date of supply.
19 | Technical Specification | 83 of 154 | 19.13 | The control and relay panel unit shall be warranted for minimum of 2 (Two) years against all material/ manufacturing defects and workmanship. | The control and relay panel unit shall be warranted for minimum of 2 (Two) years against all material/ manufacturing defects and workmanship from the date of supply.
20 | Technical Specification | 97 of 154 | 20.8 | All switchyard equipment shall be warranted for minimum of 2 (Two) years against all material/ manufacturing defects and workmanship. | All switchyard equipment shall be warranted for minimum of 2 (Two) years against all material/ manufacturing defects and workmanship from the date of supply.
21 | Technical Specification | 125 of 154 | 12.2.2 | As specified above, the MMS support shall project minimum 200mm above FGL (Finished grade level) to avoid any damage to the MMS column/sub support due to direct contact of rain water/ surface run-off. This shall be ensured through either single stage construction of entire pile length including portion above FGL or by providing a collar (to be cast in second stage) which shall project min. 75mm in plan beyond the pile face and shall extend min. 250mm below GL. | As specified above, the MMS support shall project minimum 200mm above FGL (Finished grade level) to avoid any damage to the MMS column/sub support due to direct contact of rain water/ surface run-off. This shall be ensured through either single stage construction of entire pile length including portion above FGL or by two stage construction.
22 | Technical Specification | 132 of 154 | 13.34 | The MMS shall be designed to optimize tilt angle and elevation to minimize selfshading and maximize the capture of diffuse light by Bifacial Modules. The Bifacial Module frames shall be rail-edge mounted in landscape configuration to minimize losses. | Void.
23 | Technical Specification | 132 of 154 | 13.32 | The bidder should design the structural height considering the highest flood level at site and the finished grade level. The minimum clearance between the lower edge of the module and the finished grade shall be the higher of (i) Highest flood level + 100mm and (ii) 1000 mm, as applicable. | The bidder should design the structural height considering the highest flood level at site and the finished grade level. The minimum clearance between the lower edge of the module and the finished grade shall be the higher of (i) Highest flood level + 100mm and (ii) 500 mm, as applicable.
24 | Technical Specification | 132 of 154 | 13.33 | The length of one unit (Table) of MMS shall not generally be more than 20m. | The length of one unit (Table) of MMS shall not generally be more than 30m. Effects of temperature variation shall be duly considered in the MMS design.
25 | Technical Specification | 144 of 154 | 34.3 | In case of transformer oil tank capacity more ≥ 20000 litres, the soak pit shall be connected to a separate burnt oil pit through discharge pipe (300 mm dia) and shall be suitably sized to accommodate full oil volume (excluding free board above inlet pipe) of the transformer connected to it, without backflow. In this case the capacity of the soak pit may be reduced to min. 1/3rd of the total transformer oil volume. The burnt oil pit shall be further connected to oily water drainage system. The water shall be discharged into the nearest drain by gravity flow or pumping after suitable treatment as per statutory and code provisions. | In case of transformer oil tank capacity more ≥ 5000 litres, the soak pit shall be connected to a separate burnt oil pit through discharge pipe (300 mm dia) and shall be suitably sized to accommodate full oil volume (excluding free board above inlet pipe) of the transformer connected to it, without backflow. In this case the capacity of the soak pit may be reduced to min. 1/3rd of the total transformer oil volume. The burnt oil pit shall be further connected to oily water drainage system. The water shall be discharged into the nearest drain by gravity flow or pumping after suitable treatment as per statutory and code provisions.
26 | Technical Specification | 145 of 154 | 34.6 | The area shall be provided with galvanized chain link fence of height min 1.8m with 3.5m wide gate. The specifications for fencing shall be similar to those specified under Cl. No. 31.3 except fence post which shall be of MS angle (ISA 65x65x6) spaced at 2.5 m c/c. | The area shall be provided with galvanized chain link fence of height min 1.8m with 3.5m wide gate. Fence post which shall be of MS angle (ISA 65x65x6) spaced at 2.5 m c/c. The fencing shall be of Chain link (GI or poly coat GI as specified) mesh fabric with internal, corner and stay posts. Intermediate, corner and stay posts shall be supported with min. 300 mm dia. and 850 mm deep (below GL) piles in cement concrete (nominal mix 1:1:2). The column posts shall be extended in to the pile up to 800mm with 50mm cover at the bottom. The pile shall project 150mm above GL. The intermediate, corner and stay posts shall be supported by angle struts that shall have the same foundation as that of the main posts.
27 | Technical Specification | 146 of 154 | 35.1 | Module cleaning procedure and pressure requirement at discharge point shall be as per the recommendation of PV module manufacturer. However, discharge pressure at outlet shall not be less than 50kg/cm2 (5 MPa) | Module cleaning procedure and pressure requirement at discharge point shall be as per the recommendation of PV module manufacturer. However, discharge pressure at outlet shall not be less than 5kgf/cm2 (0.5 MPa)
28 | ANNEXURE – D MANDATORY SPARES | 1 of 5 | 3 | String Monitoring Unit - 1% of total supply SMU Communication Card - 1% of Total supply | String Combiner Box - 1% of total supply
29 | Annexure F - Procedure for Plant Testing, Commissioning and Documentation | 16 of 21 | 6 | Battery Energy Storage System | Void
30 | Annexure G - Operations & Maintenance Agreement-Annexure 2 | 39 of 47 | 1.C | C. Capacity Utilization Factor (CUF) for Solar Plant shall be calculated as per the following formula. | C. Capacity Utilization Factor (CUF) for Solar Plant shall be calculated as per the following formula.
31 | Annexure C - PG Test Procedure | 10 of 10 | A | Liquidated Damages for Shortfall in PR For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service and absolute value of O & M Contract) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance. Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made. | Liquidated Damages for Shortfall in PR For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance. Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made.