## Pre Bid Query
Tender for setting up of grid connected 30 MW Floating Solar PV (FSPV) plants on raw water reservoirs of DVC Thermal Power Plants at Koderma, Mejia and Raghunathpur Thermal Power stations
SECI/C&P/PMC/11/0002/2022-23
Sl. No. | Organisation | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 | M/s BHEL | SECTION-VII: TS | 132 of 146 | 28.3.3.1 | Re. Density > 0.9 Environmental Stress-Cracking Resistance, F50 (hrs.) > 500 Secant Flexural Modulus at 2% Strain > 1000 Mpa Tensile Strength at Yield > 27 Mpa Compressive Stress at Yield > 10 Mpa More than 50% of its original break elongation after 10,000 hours exposure | The requirement given for HDPE is much higher than the current Industry practices used for Floating solar platforms. This will increase the cost of HDPE floating platforms which is around 30-40 % of the cost of whole FSPV. May kindly review the required values as per current market availability: Re. Density - 0.90-0.96 (g/cc) Environmental Stress-Cracking Resistance: for 48 Hrs with zero cracking Secant Flexural Modulus at 2% Strain > 750 Mpa Tensile Strength at Yield > 22 Mpa Compressive Stress at Yield- not required Elongation at yield> 8 % | Technical | Kindly refer Amedment -1
2 | M/s BHEL | SECTION-VII: TS | 133 of 146 | 28.3.3.1 | UL 94 or Equivalent IEC/ISO standard: Standard for Safety of Flammability of Plastic Materials for Parts in Devices and Appliances testing | This stanndard is not available readily. Please provide. | Technical | It is the responsibility of the bidder to arrange standards mentioned in the tender document. The terms and conditions of the tender document shall prevail.
3 | M/s BHEL | SECTION-VII: TS | 133 of 146 | 28.3.3.1 | For design of anchoring and mooring system, the following standards may referred (for guidance) – API RP 2SK, API Spec 2F, API RP 2I, API RP 2MIM & BS 6349-6. | Please add API RP 2A for floater strength verification, spreader bar design & pad eye design. Also DNV-RP-C205 for environmental loads shall be added. | Technical | Kindly refer Amedment -1
4 | M/s BHEL | SECTION-VII: TS | 133 of 146 | 28.5 | The floating system shall consist of multiple modular floating units/platforms and connected to the ground using anchoring and mooring system. However, the float unit shall have minimum material thickness of 3 mm, with moisture retention of less than 5%. Floating system/platform shall be fenced with vacant floats to demarcate boundary. | Achieving minimum thickness of 3 mm will increase the cost of manufacturing of Floaters which is uneconomical. Also the complete design of floaters with spreader bars and mooring system will be simulated and wherever higher thickness of floaters is required shall be provided. Request to keep it average thickness of 3 mm. All side walkway/ cable route floats will be there to demarcate the block; hence additional vacant floater will increase the costing. | Technical | Kindly refer Amedment -1
5 | M/s BHEL | SECTION-VII: TS | 134 of 146 | 28.11 | The materials used for manufacturing the floating unit shall be tested at ILAC member signatory accredited testing laboratory for ensuring the suitability of the material for use in aqueous applications. | In India, CIPET or NABL accredited labs are used to test the material. Also, manufacturers are giving their Raw Material TC. Hence, request you to allow RMTC/CIPET/NABL labs. In case not acceptable, then please provide list of ILAC member signatory accredited testing laboratories in India. | Technical | Raw material Test Reports from CIPET/NABL labs are acceptable. Please refer Amendment.
6 | M/s BHEL | SECTION-VII: TS | 134 of 146 | 28.16 | The design of complete system comprising of Floating unit and anchoring & mooring system, shall be vetted by IITs or NIOT, Chennai and submit it for PMC’s approval during detailed engineering | Please include Indian registry of Shipping (IROS) and other reputed technical universities for vetting also. | Technical | Design valifdation/vetting Report from Indian registry of Shipping (IROS) shall be acceptable. Please refer ammendment
7 | M/s BHEL | SECTION-VII: SOW | 7 of 19 | 3.2 | All documents and drawings shall be submitted to the Employer both in soft as well as hard copies (5 nos.) for review and approval. Every drawing shall also be submitted in ‘*.dwg’ format. In case of design calculations done in spread sheet, editable (working) soft copy of the spread sheet shall also be submitted along with ‘pdf’ copies during every submission. | The submission of drawing in hard copies before approval in cat-I is to be reviewed. All soft copies of the documents and drawings shall be uploaded on an online platform for the seamless review of customer. Also there can be multiple revisions for approval. The final approved set of drawings shall be submitted in hard copy. | Technical | All documents and drawings shall be submitted to the Employer in hard copies after the Cat-1/Cat-4 approval as applicable.
8 | M/s BHEL | SECTION-VII: TS | 131 of 146 | 26.6 | The Contractor shall propose a suitable module cleaning system which shall include installation of ground mounted polyethylene tank(s) of required storage capacity, pumps (including 1 No. standby pump), boat(s) for delivery of water to floating platforms, flexible hose pipes, taps, valves (NRV, Butterfly valve, Ball valve, Gate valve, PRV, scour valve etc.), Water hammer arrester(s), pressure gauge, flow meter etc. as per the planning & design. | It is suggested to lay HDPE pipelines in arrays rather to carry the water on boats. Only module cleaning manpower has to be carried out through boat or the same may also approachable through land through walkway as per site conditions. Hence, requirement of boat for delivery of water may be removed. | Technical | Module Cleaning system arrangement through HDPE pipes shall be acceptable. Please refer amendment
9 | M/s BHEL | - | - | - | Tender drawing | Please provide autocad file of reservoirs for array placement. | Technical | Please refer updated Tender Drawings
10 | M/s BHEL | - | - | - | General Query | Please provide KML file to know the exact location and boundary of the usable FSPV area. | Technical | KML file for KTPS & MTPS are alreadys submitted. KML file for RTPS shall be attached.
11 | M/s BHEL | - | - | - | General Query | Please define the indicative MQP for floaters. | Technical | MQP for floats will be finalized during detailed engineering.
12 | M/s BHEL | SECTION-VII: SOW | 11 of 19 | 4.23 | Weather monitoring station shall include but not be limited to the following:  Pyranometers – Two in Horizontal Plane for GHI and two in inclined plane for GTI – Minimum 4 (Four) Nos.  Ultrasonic Anemometer (wind speed and direction) – 2 (two) no.  Temperature Sensor (ambient and module surface) – 3 (three) nos.  Power source to the all sensors wherever required  Data Logger | Please clarify whether these quantities of WMS sensors to be supplied for all three projects together or for each project? | Technical | Kindly refer Amedment -1
13 | M/s BHEL | SECTION-VII: SOW | 4 of 19 | 1 | Power Evacuation shall be carried out through 33/66 kV grade XLPE cable of adequate size (single ckt (3 PH x 1 C + 1C spare cable) | As the evacuation voltage for all three projects is 33KV, 66KV grade cable is not required. We propose to use 33KV(E) grade cable as per IS-7098 part-2. Please confirm. | Technical | It is as per DVC requirement. Terms and condiitons of tender shall prevail.
14 | M/s BHEL | SECTION-VII: TS | 15 of 146 | 3.2 | Both solar and DC cables shall be marine grade cables complying with relevant standards | IEC 62930 / EN 50618 and IS 7098 Part II which are mentioned as applicable standards does not define marine grade cables. Please confirm the applicable standards | Technical | Kindly refer Amedment -1
15 | M/s BHEL | ANNEXURE TO BDS | 3 of 7 | 1.2 | The bidder should have experience in EPC execution of Ground mounted Solar Projects on Turnkey basis including Design, Supply (Supply of Modules & Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), Installation and Commissioning of Grid connected Solar PV Power Plant of cumulative Capacity not less than 15 (Fifteen) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission | Design, Engineering and execution of a large utility scale floating solar power plant requires susbtantial technical expertise and is thus a technical domain differenct from Ground Mounted . In the best interest of success of the proposed floating project, request SECI/DVC to specify experience of only floating solar power projects (size more than 15 MW) | Contractual | Kindly refer Amedment -1
16 | M/s BHEL | SECTION-V: SCC | 6 OF 9 | 13 | Interest bearing initial advance (OPTIONAL) of 10% of the Contract Value……………………………………………………. amounting to 110% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security. The annual interest rate shall be calculated based SBI one-year MCLR as applicable. | We request DVC/SECI to provide Interest free advance | Contractual | Kindly refer Amedment -1
17 | M/s BHEL | SECTION-V:GCC | 34 Of 81 | 32.1.1 | The Contractor shall grade/level the land identified for development of the mentioned Power Plant along with the design, procure, manufacture……………………… with interconnecting transmission system including Right of Way for Transmission Line and the comprehensive O&M of the complete facilities for the period as defined under the tender document . It is Contractor’s responsibility to coordinate with state/central agencies in order to get any permission whatsoever, required for successful development & operation of Plant till its desired life. | During Pre-bid meeting held on 01.07.2022, SECI/DVC informed that the Evacuation line is within DVC premise and no RoW is involved. SECI/DVC may kindly confirm the same. In case any approvals /eprmissions /ROW is required, SECI/DVC is requesteted to keep the same in their scope along with the associated costs/fees etc. | Contractual | Project location and entire route for power evacuation is within the DVC KTPS Project area. Hence, no ROW issue is envisaged.
18 | M/s BHEL | SECTION-V: GCC | 107 OF 247 | 32.1.4 | The Contractor shall acquire in its name all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings………………..but not limited to, the right of way for the access to site and for erection of transmission lines as applicable, visas for the Contractor’s and Sub-Contractor’s personnel and entry permits for all imported Contractor’s Equipment. The Contractor shall acquire all other permits, approvals and/or licenses that are not the responsibility of the Owner and that are necessary for the Performance of the Contract. | - | Contractual | Query not clear
19 | M/s BHEL | SECTION-V: SCC | 6 of 9 | 10 | In the matter of connectivity of Plant to DISCOM’s substation, the Owner will take the necessary connectivity permission, however, all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc. are to be taken by the Contractor. All the required fees including statutory fees, Supervision charges etc. shall be paid / born by the contractor | - | Contractual | Query not clear
20 | M/s BHEL | SECTION-VI: SAMPLE FORMS & FORMATS | 166 OF 247 | FORM F-24 | POWER OF ATTORNEY FOR BIDDING COMPANY | We request DVC/SECI to allow to submit General Power of Attorney duly signed by Completent authority at BHEL. (Ref. Annex A for the General Power of Attorney) | Contractual | All such general PoA cases shall be dealt on case to case basis. However in general such authorized GPAs are acceptable.
21 | M/s BHEL | SECTION-V: SCC | 157 OF 247 | 4(10) | Cutting of trees, bushes and vegetation from site (including permission from local authorities) and disposal thereof. The site should be maintained in vegetation free condition during erection stage (at any point of time) i.e., up to start of O&M Contract. | We request SECI/DVC to include arranging permissions for and cutting of trees, bushes and vegetation in their scope. | Contractual | Cuting of trees, bushes and vegetation (if required) will be under bidders scope. DVC will fecililate the necessary permission if so required.
22 | M/s BHEL | SECTION-IV: GCC | 103 OF 247 | 28.1 | The Contractor shall provide and maintain an office at the site for the accommodation of his agent and staff (With meeting room) and such office shall be open at all reasonable hours to receive instructions, notice or other communications……………………………………............................................................................................ Further contractor shall also provide & ensure availability of required Vehicle (Preferably SUV Segment Vehicles requiring Off -Roading) with driver and fuel/Maintenance/Consumables etc for the purpose of Mobility in and around the site for official purposes for the PMC & its staff. The vehicle as mentioned is to be provided during project construction and O&M period and inspection by SECI as per requirement, failing which SECI shall have full right for alternate arrangement at the risk & cost of the contractor. | We request SECI to further clarify/elaborate on this clause as also discusssed during the pre-bid meeting held on 01.07.2022 | Contractual | The vehicle required by SECI will be for the visit of SECI officials to the site during and before the operational acceptance of the plant. The vehicle deployed by the Contractor on the site for their use can also be used for such visits from SECI officials.
23 | M/s BHEL | GENERAL | - | - | - | We request SECI/DVC to provide the height & location of Chimneys in vicinity vis-à-vis the reservoir or the proposed floating soalr power plant . This is critical to factor in the shadow effect of the chimneys on the solar modules | Technical | Maximum Chiney height: MTPS: 275 Metres, RTPS: -275 Metres and KTPS:- 275 Metres. For location of chimnies of respective stations please refere Google earth/map.
24 | M/s BHEL | GENERAL | - | - | - | We request SECI/DVC to provide the GHI data laong with the tender itself similar to the practise followed by other developers viz. NTPC, SJVN so that all the bidders are brought at par wrt the design of the project | Technical | Choosing the GHI data source is the independent decision of the biddder. SECI provides Radation correction factor (RCF) based on the Refernce GHI mentioned in the O&M Contract. The same has been amended for better clarification.
25 | M/s BHEL | GENERAL | - | - | - | We requerst SECI/DVC to share a route survey with least obstacles for the UG cable from the solar power plant to the terminal substation Please also inform whether the existing cable trays could be used for carrying the ecacution cable or new trays have to be built (if required) | Technical | The route survey for the UG Cable from the solar plant to terminal station will be under the Contractor scope. Further, if space is available in the existing cable tray it will be provided upon request to DVC.
26 | M/s BHEL | SECTION-IV: GCC | 148 of 247 | - | - | We requerst SECI/DVC to share a route survey with least obstacles for the UG cable from the solar power plant to the terminal substation Please also inform whether the existing cable trays could be used for carrying the ecacution cable or new trays have to be built (if required) | Technical | The route survey for the UG Cable from the solar plant to terminal station will be under the Contractor scope. Further, if space is available in the existing cable tray it will be provided upon request to DVC.
27 | M/s BHEL | SECTION-IFB | 4 of 11 | 4 | The Cells and Modules used in this tender shall be sourced only from the Models and Manufacturers included in the List-I (Solar PV Modules) of ALMM Order, Annexure-I of the OM, issued by MNRE on 10th March 2021 which will be updated by MNRE from time to time. The modules to be supplied under this tender, shall be from the List-I of the ALMM order applicable on the date of invoicing of such modules.- | Request to please stipulate ALMM modules list as on date of commissioning rather than date of invoicing | Contractual | The terms and conditions in the tender document shall prevail.
28 | M/s Lumino | IFB | 11 of 11 | 6 & 7 | Owner will release NOA/ LOI/ LOA for LSTK (Lump Sum Turn Key)/ EPC (Engineering, Procurement & Commissioning) to the successful bidder. The NOA/ LOI/ LOA for LSTK/ EPC job shall be awarded in following respective parts as mentioned briefly below: - (i) First Contract (Supply Part): For providing the Ex Works Supply, materials including mandatory spares and any other supplies specified in the Tender Documents under the scope of Supply. (ii) Second Contract (Service Part): For all services i.e., including Transportation and Insurance of all Equipment’s till site, Unloading, Storage, Handling at Site, Civil Works, Design, engineering, Erection, Installation, Testing and Commissioning including Performance Testing in respect of all the Equipment’s supplied under the scope of Supply and any other services specified in the Contract Documents. (iii) Third Contract (O&M Part): For providing Comprehensive operation & maintenance of the Solar PV plant for 10 (Ten) years from the date of Operational Acceptance, as detailed in technical specification including supply and storage of all spare parts, consumables, repairs/ replacement of any defective equipment etc. However, the above-mentioned contract award methodology may be modified/ changed based on specific project requirements and upon sole discretion of Owner. | Is the Contract vale need to be quoted include of GST and all other applicable Taxes, Please clarify . Contract award Methodology post order changing will change theStrategy of Bidder , hence request provide any change of Contract Methodology before submission of tender well in advance before 15days | Finance | Bidders are strictly required to quote only as per the Schedule of Rate supplied with the tender document. This is a general clause and if in case of any change in the Contract Methodology during the tendering process, bidders will be provided sufficient time for submitting their revised bid.
29 | M/s Lumino | ITB | 6 of 45 | 2.4 | Bidder shall not be affiliated with an entity: (i) that has provided consulting services related to the work to the PMC/ Owner during the preparatory stages of the work or of the project of which the works/ services forms a part of or (ii) that has been hired (proposed to be hired) by the PMC/ Owner as an Engineer/ Consultant for the contract. | Please declare the PMC Consutant or going to apoint so that the bidder may understand whom not be affiliated | Contractual | All such PMC/consultant cannot be declared upfront and are engaged on requirement basis only.
30 | M/s Lumino | ITB | - | 32.4.2 | At least one week prior to e-RA, an advance intimation regarding the date and time of the e-RA will be sent by email to all bidders whose technical & financial bids have been opened and found to be qualified. However, from this advance intimation it shall not be construed by the bidders that they have been shortlisted for e-RA. Further at least two hours before the schedule start time of e-Auctioning, a system generated email for invitation for e-Auctioning will be sent to all those bidders only who have been shortlisted based on the criteria mentioned. | The e-reverse auction intimation along with the base price and decrement value request to provideatlease 3working days in advance for cost work out purpose . The decrement value in the tender mentioned with Rs. 10,000,00 if this is the decrement value then no decrement value required please confirm | Contractual | Techno-commercially and Financially qualified will be notified well before the e-RA date (atleast one week prior to e-RA date) which will provide them sufficient time to work on their cost. Further as clearly specified in the tender document decremnt will bew in the multiples of INR 10 lakhs only. This means the bidders can reduce their prices downwards in the multiples of 10 lakhs to beat the L1 cost.
31 | M/s Lumino | GCC | 12 of 81 | 2.1.b | Contractor, if necessary, shall build other temporary access roads to the actual site of construction for his own work at his own cost. The Contractor shall be required to permit the use of the roads so constructed by him for vehicles of any other parties who may be engaged on the project site. The Contractor shall also facilitate the construction of any permanent roads should the construction thereof starts while he is engaged on this work. He shall make allowance in his Tender for any inconvenience he anticipates on such account. Non-availability of access roads, railway siding and railway wagons for the use of the Contractor shall in no case condone any delay in the execution of work nor be the cause for any claim for compensation against the PMC/ Owner. | Bidder understand all the three site Raw water where the project will happened is approachable, please confirm | Contractual | As of now all the sites that are mentioned in the tender document are approachable by road, but if construction or renovation of such roads is required , it will be under the Contractor's scope and DVC will assist them in the due process.
32 | M/s Lumino | GCC | 12 of 81 | 2.3 | Contractor will have to make his own arrangements for supply of water to his labour camps and for works. The water quality should be suitable for use in civil construction work. All pumping installations, pipe network and distribution system will have to be carried out by the Contractor at his own risk and cost. Alternatively, the PMC/ Owner at his discretion may endeavor to provide water to the Contractor at the PMC's/ Owner’s source of supply provided the Contractor makes his own arrangement for the water meter which shall be in custody of the PMC/ Owner and other pipe networks from source of supply, so as not to interfere with the layout and progress of the other construction works. In such case, a separate accounting shall be maintained for billing purpose on monthly basis. However, the Owner does not guarantee the supply of water and this does not relieve the Contractor of his responsibility in making his own arrangement and for the timely completion of the various works as stipulated. | Bidder understand that the permission for making bore well will be provided by client if water borewell making by own. As a optional installing of Meter the Owner providing the water then please clarify what is the charge applicable for water consumption | Contractual | Supply of Water: Bidder(s) are encouraged to extract ground water for construction as well as O&M activities by making borewell at their own cost and means. In case water for construction and O&M acitivities is supplied by DVC, contractor shall have to pay water charges on cost basis.
33 | M/s Lumino | GCC | 12of 81 | 2.4.1 | Contractor has to arrange for the construction power supply of their own. However, subject to availability, PMC/ Owner may provide access to the nearest available point in his location for supply power at only one point, from where the Contractor will make his own arrangement for temporary distribution through a temporary energy meter (sealed by PMC/ Owner). All the works will be done as per the applicable regulations with information to the Engineer-in-Charge/Project Manager. The | Bidder understand that the permission for arrange the service line from local DISCOM will be provided by client if arranging power in this way. As a optional installing of Meter the Owner providing the Power supply then please clarify what is the charge applicable for Electricity consumption | Contractual | Supply of Electricity: In case power during construction/O&M period is provided by DVC as per relevant clauses of NIT, the contractor shall have to pay charges as per applicable retail tariif of DVC at the time of drawl. The rate of Power supply shall be guided by distribution tariff of DVC for respective state consumers.
34 | M/s Lumino | GCC | 31 of 81 | 28 | The Contractor shall provide and maintain an office at the site for the accommodation of his agent and staff (With meeting room) and such office shall be open at all reasonable hours to receive instructions, notice or other communications. The contractor shall make provisions and arrangements at site locations for temporary office (Portacabin) including all basic amenities having electricity, furniture, Air Conditioning, Sanitation, toilet facilities, etc. at his own cost on behalf & purpose of the PMC and his staff and shall get the clearance of local authorities for setting up/construction of such facilities. Bidders are required to consider all such temporary office construction cost into his account, while bidding. These facilities shall be provided till the final handing over of the project to the Owner. The contractor shall ensure that the area is kept clean and sanitary conditions are maintained as laid down by the local authorities controlling the area. Further contractor shall also provide & ensure availability of required Vehicle (Preferably SUV Segment Vehicles requiring Off Roading) with driver and fuel/Maintenance/Consumables etc for the purpose of Mobility in and around the site for official purposes for the PMC & its staff. The vehicle as mentioned is to be provided during project construction and O&M period and inspection by SECI as per requirement, failing which SECI shall have full right for alternate arrangement at the risk & cost of the contractor | Bidder undersatnd the dedicative photocabin to be provided to the PMC Consultant for all three site minimum size of 20feet with mimum 5seating arrangement up to 11years Including Project and O&M tenure Also bidder understand that the dedicative SUV vehicle during project duration around tenure of 11years may provide considering of project duration . Please provide the details how much km travelling will be taken for considereation for per day | Contractual | The vehicle required by SECI will be for the visit of SECI officials to the site during and before the operational acceptance of the plant. The vehicle deployed by the Contractor on the site for their use can also be used for such visits from SECI officials. The running kms of the vehicle are subjective in nature and fully depends on the site locomotive requirements and cannot be predicted as such.
35 | M/s Lumino | GCC | 34of 81 | 32.1.1 | The Contractor shall grade/level the land identified for development of the mentioned Power Plant along with the design, procure, manufacture (including associated purchases and/or subcontracting), install, commission and complete the Facilities, carry out the Guarantee tests with due care and diligence in accordance with the Contract along with interconnecting transmission system including Right of Way for Transmission Line and the comprehensive O&M of the complete facilities for the period as defined under the tender document . It is Contractor’s responsibility to coordinate with state/central agencies in order to get any permission whatsoever, required for successful development & operation of Plant till its desired life | The bidder undersatnd all the three sites coming under the permisses of M/s DVC hence there was no ROW issue is there interms of transmissio n line work and Solar EPC Work please confirm As the project developed by M/s DVC bidder understand that the all the state and central government approval will be taken care by them upto life time the required document input will be provided by the contractor up Project duration and O&M duration of 10 Years Please clarify | Contractual | Yes all three premises comes under DVC. Kindly refer clause 32.1.2 of Section - IV "General Conditions of Contract" of the tender document for refering to various approvals and clearances to be obtained by the contractor on behalf of owner.
36 | M/s Lumino | GCC | 34 of 81 | 32.1.3 | The Contractor shall acquire, on behalf of Owner, in the Owner’s name, all permits, approvals and/or licenses from all local, state or national government authorities or public service undertakings in the Country/State where the Site is located that are necessary for the setting up of the Plant & operation of Plant till its desired life as mentioned under the Contract, including, but not limited to, entry permits for all imported Owner’s/PMC’s Equipment (if any). In this regard, any document required from Owner/ PMC shall be intimated at least 10 days prior to submission. Contractor has to ensure safe keeping of the documents and diligent use. It is the responsibility of the Contractor to safe keep and return all the original approvals, permits, licenses, certificates and other relevant document generated as a result of the setting up of project and comprehensive O&M process to the Owner. | Bidder understand that all documentation support will be provided by bidder the required communication with state and central agency will be taken care by PMC/Owner and the required permit fees also pay by them . Please clarify | Contractual | No the documentation fecilitation will be done by Owner and all other necessary formalities in obtaining such approvals/permits is under the scope of contractor.
37 | M/s Lumino | TS | 7 of 146 | 2.7 | The designed array capacity at STC shall be suitably determined to meet the proposed guaranteed generation output at the point of interconnection by the contractor in his bid. The contractor shall take care of first year degradation also by installing additional DC capacity as the CUF calculations will not factor the first-year degradation of the modules. | The DC Capacity only to be considered as defined by client .since this was clear that the module STC condition at the field will not meet due to Ambient Temperature. Hence there was not requirement of additional DC Capacity except mentioned in the tender . Kindly clarify if the additional DC Capacity to be installed above the mention DC Capacity as per tender | Technical | DC Capacity mentioned in Scope of Works is the minimum DC capacity. Contractor has to design the system in order to achive the required CUF.
38 | M/s Lumino | TS | 8 of 146 | 5 | Approval of document neither relieves the Vendor/ Contractor of his contractual obligations and responsibilities for correctness of design, drawings, dimensions, quality & specifications of materials, weights, quantities, assembly fits, systems/ performance requirement and conformity of supplies with Technical Specifications, Indian statutory laws as may be applicable, nor does it limit the PMC/ Purchaser’s rights under the contract) | Please clarify once the document approved from Client end dual checking of supporting documents and site measurements and during execution of work client asking for additional change will delay the project , so request to strict on the drawing if the revision asked to change after approval and prcurement of materials will impact the cost and time line of project. So please advice and elabrate this clause | Technical | The terms and conditions in the tender document shall prevail.
39 | M/s Lumino | TS | 11 of 146 | 1.3.1 | The PV Modules shall be glass-glass type, with minimum 2 mm glass thickness on each side. | The meaning of glass-glass type need to be clarifiied and also please cofnirm this type of module available in Multi and Mono Crystaline of ALMM approved list if yes then what is the Maximum Wp capacity available in both module kindly confirm | Technical | Glass-Glass type modules are those PV modules with glass present on both front and back side.The rationale behind using these modules in FSPV is coarse environmental conditions such as high humidity. PV Module needs to be ALMM approved until the date of invoicing.
40 | M/s Lumino | TS | 37 of 146 | 7.3.1 | The switchgear panel shall be free standing, floor mounted, single front, single tier fully compartmentalized, metal enclosed construction. Each panel shall have separate compartments for circuit breaker, bus bars, cable termination and auxiliary circuit. | Request to allow to use 33KV Outdoor VCB Panel also along with CRP and request to provide the appropriate area to Make switchyard near MCR of Floating solar projects location . Also request to allow to Use Indoor /Outdoor RMU based on the suitability | Technical | The terms & Conditions of the Tender document shall prevail. However, vacant area for the Switchyard & MCR shall be decided in consultation with DVC.
41 | M/s Lumino | TS | 64 of 146 | 17.1 | Power Transformer 33/132KV & NIFPS | As per LIL understanding there was no requirement of 33/132KV Power transformer and NIFPS, since the power transformer & NIFPS technicalspecification provided please clarify the requirement to understand | Technical | Document containing Technical Specifications is a general document. Please refer Special Technical Specifications. There is no requirement on Power Transformer.
42 | M/s Lumino | TS | 84 of 146 | 20 | 132 kV Switchyard Equipment | As the Power evacuation is 33KV Level but in Technical specification the 132KV Switchyard related information provided is the requirement of this project please clarify | Technical | Document containing Technical Specifications is a general document. Please refer Special Technical Specifications. There is no requirement of 132 kV Switchyard system.
43 | M/s Lumino | TS | 98 of 146 | 21 | This specification covers design, supply and installation of uniformly Illumination system along the peripheral & internal roads, main control room & inverter rooms, switchyard and other facilities including entry points/gate(s) inside the plant area. | The peripheral and Internal road illumination requirement mentioned inth tender document . Please clarify howmany Outdoor Light pole to be considered is the requirement of Street light pole surrounding and middle of the Water reservior whereever the road gone . | Technical | Kindly refer Amedment -1
44 | M/s Lumino | TS | 109 of 146 | 28 | The Contractor has to do the power evacuation and integration to and with the designated substation via either overhead transmission line or underground cables or cable through existing cable trestle/trench subject to availability at specified grid voltage with all necessary infrastructure such as protection switchgears and metering systems as per the requirement of the STU/PMC. The Contractor shall get the route approval from the PMC and STU prior to start of the construction. Any changes in the route or scheme at any point of the time prior to commissioning shall be complied without any additional cost to the PMC. | As per the tender document the power evacuation is proposed through Under ground , but as per Technical clause no.28 Over head Transmission line also may allowed kindly clarify with the option and provide with the perfect route to avoid the imact on incerase of transmission line or other impact . The last minumtes movement before commissioning the scheme may changed will not help bidder to participate on cost effective manner, hence the power evacuation method along with clear route and requirement need to be clarify during pre-bid meeting stage to optimize the system . Also the requirement of cable tray need to be cleared whether incase of UG cable power evacuation then the provision of new cable tray need to make for full 2KM length or existing available space of cable tray may used . | Technical | Pleaae refer Special technical Specifications. Power evacuation shall be done through UG cable only. Bidders are required to survey the area & evacuation route identification. DVC shall facilitate the same.
45 | M/s Lumino | TS | 110 of 146 | 1.2 | This excludes design, supply and installation of Galvanised 220 kV and 132 kV Transmission Line towers, Tower extensions & accessories and 11 kV, 22kV & 33 kV transmission poles & accessories which shall be designed following latest guidelines of respective SEB (State electricity board) and got approved before execution. In absence of SEB/ STU guidelines REC (Rural electrification corporation) standards may be followed. Poles at corner with angle > 100 shall be provided with 4-pole structure or lattice tower. Use of PCC spun poles is not acceptable. Approved copies of these designs & drawings shall be submitted to the PMC for reference and record. | The Power evacuation is through Over head line then the scope is in Client side please clarify | Technical | Please refer Special technical Specifications. Power evacuation shall be done through UG cable only. Bidders are requirested to survey the area & evacuation route identification. DVC shall help in the same.
46 | M/s Lumino | TS | 116 of 146 | 5.8 | The report shall also include ground water analysis (water sample collected from bore well) to ascertain its suitability for construction purposes, recommendations for type of cement, grade of concrete & minimum cement content as per prevalent soil characteristics with respect to presence of aggressive chemicals and environment exposure conditions as per relevant BIS specifications. However, minimum grade of concrete shall be M25 (M30 in coastal areas/ marshy soil) for all RCC works except liquid retaining structures like underground water tank etc. where minimum grade of concrete shall be M30 (M35 in coastal areas/ marshy soil). Cement higher than 43 Grade, shall not be used in construction. | The Concrete grade level as provided in the tender ,please clarify as all the proposed flaoting solar project inside the thermal power station near to that the existing building already available, in reference to that request to confirm the concerete grade of all three projects please | Technical | The terms and conditions in the tender document shall prevail.
47 | M/s Lumino | TS | 117 of 146 | 7.2 | The Approach road connecting nearest public road and the Main gate shall be of 4.0m wide carriage way with 0.5m wide shoulders on either side. The access road connecting Main gate and MCR and internal access road(s) connecting MCR to various facilities/ buildings/ open installations shall be of 3.0m wide carriage way with 0.5m wide shoulders on either side. The top elevation of approach road (TOR) and access pathways shall be minimum 200 mm above FGL to avoid flooding during rains. The roads shall be provided with alongside drains as per design requirements of drainage system to avoid flow of storm water over the road. | As per the site visit MTPS already have the Morrum Road , RTPS & Koderma have bitumin roadthrough out the Water reservior periphery . Hence only MCR, ICR and Main road connecting to be done. As per the tender the WBM Road has been propsoed request to considered the Concrete also as optional along with WBM with the same dimention and thickness of minimum 150 to 200mm | Technical | The terms and conditions of tender shall prevail. However, superior grade material if proposed by the contractor may be acceptable. However, No extra cost shall be paid on the account of the same.
48 | M/s Lumino | TS | 120 of 146 | 9 | The plant peripheral boundary shall be provided with either Chain link or barbed wire fencing or masonry boundary wall as specified. | As all three project location is inside the Boundary of Client Thermal Power station is the Boundary Fencing is really required excpet the Outdoor Switchyard please clarify | Technical | Please refer Special Technical Specifications: There shall be no requirement of boundary wall/fence, main gate & floating fence. However, fencing & gate shall be required for the transformer yard.
49 | M/s Lumino | TS | 121 of 146 | 9.6 | The plant peripheral boundary shall be provided with either Chain link or barbed wire fencing or masonry boundary wall as specified. | As all three project location is inside the Boundary of Client Thermal Power station please clarify is there that the separate Main Gate is required except for the outdoor Switchyard Gate | Technical | Please refer Special Technical Specifications: There shall be no requirement of boundary wall/fence, main gate & floating fence. However, fencing & gate shall be required for the transformer yard.
50 | M/s Lumino | TS | 131 of 146 | 26.3 | The Contractor shall estimate the water requirements for cleaning the photovoltaic modules at regular frequency in order to operate the plant at its guaranteed plant performance. However, minimum consumption of 2 litre / sq.m of surface area of SPV module shall be considered in estimation of required quantity of water storage. | 1. During the O&M Period for cleaning of module the water will be provided by Client in Free of Cost . 2. If the proposed Water reservoir having the water matching the TDS level as per the OEM recommentation shall we use the same reservoir water for Module cleaning or separate pipe line to be made please clarify 3. Is the RO plant requirement is there Please calrify above three points for understanding | Technical | 1. Water will be provided to the Contarctor upon chargable basis by DVC as mentioned in the tender document. 2. Please refer Amendment. 3. Terms and Conditions of the tender shall prevail.
51 | M/s Lumino | TS | 237 | MCR Drawing | MCR Elevation and Sectional Drawing | Please clarify whether the same Main Control room Drawing to be considered for all three site construction work please clarify | Technical | Yes, it is applicable to all the three sites separately.
52 | M/s Lumino | TS | 4 of 19 | 1 | Performance Ratio (PR) at 33 kV side of Plant Substation is 84% and Capacity Utilization Factor (CUF) at 33 kV side of Plant substation is 22.5% | The PR and CUF to be calculated from the actual Irradiation level instead of Initial PV Syst estimated PR and CUF. Also the Grid failure and the Break down of Equiments must be considered as actual. Please advise and clarify . Also plant substation is meaning of before Power evacation point at plant end switchyard which is planned near to the water reservoir please confirm | Technical | These are the required PR & CUF. Considering these values, system has to be designed. While calculating the CUF during O&M, plant outage due to grid failre shall be taken into account. Breakdown of the equipments is the responsibility of the Contractor. Yes, CUF & PR are valid upto the plant substation present near the reservoir.
53 | M/s Lumino | General | - | - | General | The Transmission line route considering of UG cable the existing Tray is not free to lay the solar project Powerevacuation line, please clarify with proposal of hindrance free route and the Requirement of Cable trays and civil work if required | Technical | Power & communication cable laying for the solar project will be through existing cable tray/trench (whereever anvailable) and through newly constructed (under scope of this contract) cable tray/trench as per requirment of the project and NIT specification. Bidders are required to asses site requirment by visiting the project sites.
54 | M/s Lumino | General | - | - | General | Main Control room, Local Control room and Outdoor Switchyard area was provided from client end which was not proposed in the reference drawing please clarify | Technical | A reference drawing for MCR has already been attached. Required area shall be decided in consultation with the selected bidder.
55 | M/s Lumino | General | - | - | General | At MTPS 33KV Bay space available but for extention the existing road also to be utilized. Request to provide hindrance free space to make bay arrangement | Technical | The bay bay construction is proposed in the existing 33 KV switchyard of MTPS for which access (road) is available. Any further extension if envisaged for completion of the project sahll be in the scope of the contract.
56 | M/s Lumino | General | - | - | General | At RTPS its has been observed that all VCB /SF6 SAS control type please clarify normal type VCB withCRP control required or SAS system control CRP required | Technical | The terms and conditions in the tender document shall prevail.
57 | M/s Lumino | General | - | - | General | During the site visit it has been understand that surrounding of Reservoir the trees and Bushes are there to make the mooring arrangement and avoid shadow the same to be removed request to provide the permission for the same also clarify the incase of any change in scope | Contractual | If any such permission required, will be taken care by DVC.
58 | M/s Lumino | General | - | - | General | Near to the reservoir it has been observed the Chimney and existing tall structures are observed, request to confirm there was no reflection of shadow due to the same . | Contractual | Maximum Chiney height: MTPS: 275 Metres, RTPS: -275 Metres and KTPS:- 275 Metres. For location of chimnies of respective stations please refere Google earth/map.
59 | M/s Quant Solar | Section 1 | 7 | Clause 4 | The Cells and Modules used in this tender shall be sourced only from the Models and Manufacturers included in the List-I (Solar PV Modules) of ALMM Order, Annexure-I of the OM, issued by MNRE on 10th March 2021 which will be updated by MNRE from time to time. The modules to be supplied under this tender, shall be from the List-I of the ALMM order applicable on the date of invoicing of such modules. | There are some PV module manufacturers, who have applied for getting included in ALMM list and should be included shortly. These are not in the List-1 of MNRE issuedon 10th March 2021. The Cells and Modules used in this tender shall be sourced only from the Models and Manufacturers included in the updated list (Solar PV Modules) of ALMM Order, issued by MNRE. The modules to be supplied under this tender, shall be from the List of ALMM Order updated at the time of invoicing of modules. | Contractual | Kindly refer to clause 4 of Section -I 'IFB' which quotes : "The .......................................................... modules to be supplied under this tender, shall be from the List-I of the ALMM order applicable on the date of invoicing of such modules. Bidders shall also provide a disclosure regarding that they are aware of binding provisions of the ALMM order and the list(s) thereunder, while quoting for the tender."
60 | M/s Quant Solar | Annexure to BDS- Qualifying Requirements | 68 | Clause 1.2 ( Technical Eligibility Conditions) | IB - the bidder should have experience in EPC execution of Ground mounted Solar Projects on Turnkey basis including Design, supply (Supply of Modules & Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), installation & commissioning of at least 02 (Two) Grid connected Solar PV Power Plant Projects having an individual capacity of 3 (Three) MW or above in last seven Financial years | EPC of Floating Solar Projects have not been considered in the experience here. Further, in JV , the cumulative work experience of 2 or 3 parties has not been considered. This will narrow down the participation. It is requested to : 1.) Keep the Floating Solar EPC too as a part of the experience. 2.) consider cumulative experience of 2/3 parties in JV in EPC projects 3.) Consider 6(Six) Grid connected Solar PV Power Plant Projects having an individual capacity of 1 (One) MW in last seven financial years. | Contractual | Kindly refer Amedment -1
61 | M/s Quant Solar | Annexure to BDS- Qualifying Requirements | 69 | Clause 1.3 ( Financial Eligibility Conditions) | The Minimum Average Annual Turnover (MAAT) of the bidder in the last three financial years (i.e. FY 2019-20, 2020-21 and 2021-22) should be INR 80,43,00,000/- (Indian rupees Eighty crores forty-three lakhs only). | The MAAT of INR 80,43,00,000 shall narrow down participation and will exclude good players who have executed projects in this range of capacities It is requested to keep MAAT requirement of INR 40,00,00,000. | Contractual | Kindly refer Amedment -1
62 | M/s Quant Solar | Annexure to BDS- Qualifying Requirements | 69 | Clause 1.3 ( Financial Eligibility Conditions) | The bidder should have a minimum Working Capital of INR 50,27,00,000/- (Indian Rupees Fifty crores twenty seven lakhs only) as per the last audited financial statement. | The Working capital of INR 50,27,00,000 shall narrow down the participation and exclue good companies who have done signifiant projects but don’t have credit line from bank of this scale. It is requested to keep Working Capital Requirements of INR 10,00,00,000 ( Ten crores) | Contractual | Kindly refer Amedment -1
63 | M/s Quant Solar | Annexure to BDS- Qualifying Requirements | 70 | Clause 1.3 ( Financial Eligibility Conditions) ( JV & Consortium Conditions) | Herein, apart from the Lead partner/member, a minimum of 25% Financial eligibility should be met individually by all other partners/members of the JV/Consortium. | A minimum requirement of 25% Financial eligibility for all the partners will exclude MSME companies, who have conributed much to the Floating Solar projects but don’t qualify 25% financial eligibility It is requested to keep a minimum requirement of 15% Financial eligibility for all the partners. It will help company like Quantsolar to participate in JV format | Contractual | Kindly refer Amedment -1
64 | M/s Quant Solar | Special Conditions of Contract | 155 | Clause 3 | The Time for Commissioning for the cumulative capacity of 30 MW floating Solar PV Power Plant at 03 different sites along with other associated equipment as per this tender document in total shall be 12 (Twelve) Months from the Date of the Notification of Award NOA/LOA/LOI. | In case of Floating Solar projects, every site offers a different set of challenges especially related to Anchoring and Plant installation. And therefore, completing three Floating Solar projects within 12 months at three different locations and in two different states will be a significant challenge The Time for Commissioning for the cumulative capacity of 30 MW Floating Solar should be atleast 18 months | Contractual | Kindly refer Amedment -1
65 | M/s Sunshore | ANNEXURE TO BID DATA SHEET (BDS) QUALIFYING REQUIREMENTS | Page 3 of 7 | 1.2 | Route I IA. The bidder should have experience in EPC execution of Ground mounted Solar Projects on Turnkey basis including Design, Supply (Supply of Modules & Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), Installation and Commissioning of Grid connected Solar PV Power Plant of cumulative Capacity not less than 15 (Fifteen) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. Route II IIA. The bidder should have experience in execution of Ground mounted Solar Projects as a Developer of Grid-connected Solar PV Power Plant(s) of cumulative Capacity not less than 15(Fifteen) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission | 1. Request to include all Grid Connected Solar Projects and not specificly Ground Mounted 2. Request to combined Route I and Route II i.e., EPC and Developer projects for meeting the 15 MW criteria | Contractual | The terms and conditions in the tender document shall prevail.
66 | M/s Sunshore | - | - | - | Other - Tehnical Specification Required | Not defined in Tender Document. Please define | Technical | All the documents have been uploaded at https://www.bharat-electronictender.com/
67 | M/s Sunshore | - | - | - | Other - Site Details | Not defined in Tender Document. Please define | Technical | All the documents have been uploaded at https://www.bharat-electronictender.com/
68 | M/s Sunshore | - | - | - | Other - Interconnection/Evacuation Facility | Not defined in Tender Document. Please define | Technical | All the documents have been uploaded at https://www.bharat-electronictender.com/
69 | M/s Sunshore | - | - | - | Other - CUF & PR Requirements | Not defined in Tender Document. Please define | Technical | All the documents have been uploaded at https://www.bharat-electronictender.com/
70 | M/s MIPL | ANNEXURE TO BID DATA SHEET (BDS) QUALIFYING REQUIREMENTS | 68 of 247 | 1.2 | 1.2 TECHNICAL ELIGIBILITY CONDITIONS | The qualification criteria for EPC (Route I) and Developer mode (Route II) have been defined separately for which bidder can qualify and bid in any of the mode. That is, a bidder either has to have 15 MW under EPC Mode or 15 MW under developer mode. We request you to kindly consider and allow qualification with mix of Route I and Route II clauses as well. For e.g., if the bidder has executed 5 MW under EPC Mode and 10 MW under Developer mode, the bidder may be qualified and allowed to bid. Kindly allow. Or We request you to kindly consider removing criteria of “last seven Financial years as on last date of bid submission” as is the case with all NTPC tenders. | Contractual | The terms and conditions in the tender document shall prevail.
71 | M/s Novus Green | TS | - | 28.17 | 28. Floating System: (Tender Document) Technical Requirements 28.17 The floating system, or sections thereof, shall be anchored using concrete blocks. Reservoir bed/embankment drilling is not permitted for anchoring/tethering. | For dead weight anchoring, the anchors must be dropped from certain height, so there is a possibility ofnreservoir bed damage as weight of the anchors will be more. So please confirm the risk scope for any damages of reservoir bed. Anchor weight will be approximately 30-40 tons, so shifting of anchors to the position will be more critical. So requesting SECI/DVC to confirm the installation procedure, if any deviations are allowed. | Technical | Safe handling and placement of Concrete Blocks(dead weight anchors) shall be the responsibilty of the contractor. Terms and conditions of tender shall prevail.
72 | M/s Vikram Solar | IFB | 6 | 2.4 | Owner reserves the option to reduce any of the above-mentioned site capacity from the overall cumulative capacity before/after award of Contract Agreement. Accordingly, the total project price will be proportionately reduced & the final project price arrived as such after reduction will be the final project price of the Contract Agreement. | We would request you to kindly restrict such changes prior to bid submission. Price bidding is a financial decesion which is based upon economies of scale associated with 30 MW capacity therefore any major reduction in MW capacity shall be detrimental to the interest of bidder. | Contractual | The terms & Conditions of the Tender document shall prevail. However, vacant area for the Switchyard & MCR shall be decided in consultation with DVC.
73 | M/s Vikram Solar | IFB | 7 | 4 | APPROVED LIST OF MODELS & MANUFACTURES: The provisions as contained in the O.M. dated 10.03.2021 issued by MNRE on the subject “Approved Models and Manufacturers of Solar Photovoltaic Modules (requirement of compulsory registration) Order, 2019-Implementation-Reg.” and its subsequent amendments and clarifications, shall be applicable for this tender. The Cells and Modules used in this tender shall be sourced only from the Models and Manufacturers included in the List-I (Solar PV Modules) of ALMM Order, Annexure-I of the OM, issued by MNRE on 10th March 2021 which will be updated by MNRE from time to time. The modules to be supplied under this tender, shall be from the List-I of the ALMM order applicable on the date of invoicing of such modules. Bidders shall also provide a disclosure regarding that they are aware of binding provisions of the ALMM order and the list(s) thereunder, while quoting for the tender. | We understand that ALMM pertains only to Modules. Cells for the Moudles are permitted to be sourced from anywhere globally as has been stated in Project's technical particulars (SOW,Page 3 of19,Technical specs) . Pls confirm. | Contractual | Kindly refer Amedment -1
74 | M/s Vikram Solar | - |  |  | Replace the existing clause by the following: The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of TechnoCommercial Bid (Envelope-I | Owing to volatality of prices, request you to kindly restrict the bid validity to 90 days | Contractual | The terms and conditions in the tender document shall prevail.
75 | M/s Vikram Solar | GCC |  | Definitions | 1.1.19 CONTRACT PRICE/CONTRACT VALUE/PROJECT VALUE means the firm value of the final quoted price, as a result of e- RA (if applicable), by the successful bidder specified in its financial proposal as the sum of individual contract value of Supply & Services (Supply of goods, F&I, Design, installation, Civil Works etc) as mentioned under the different work heads specified in the financial proposal including all the applicable taxes/ Goods & Service taxes | Pls confim if the Contract value excludes O&M as well? | Finance | Yes
76 | M/s Vikram Solar | GCC | 84 | Definitions | 1.1.48 NTP means Notice to Proceed subsequent to the placement of LOA/NOA/LOI. NTP will be issued by the owner within a maximum time frame of 90 days from the date of LOA/NOA/LOI, failing which the LOA/NOA/LO shall stand withdrawn without creating any further liability on either party. In such case EMD/PBG, as applicable submitted by the contractor shall be released | Inview of extremely volatile market prices, we have to commence project execution for timely PO placement/ordering. Hence pls restrict the NTP issuance to within 7days of issuance of LOI. | Contractual | The terms and conditions in the tender document shall prevail.
77 | M/s Vikram Solar | GCC | 92 | 17.1 | The Contractor in fixing his cost shall for all purpose whatsoever reason may be, deemed to have himself independently obtained all necessary information for the purpose of preparing his tender and his tender as accepted shall be deemed to have taken into account all contingencies as may arise due to such information or lack of same. The correctness of the details, given in the Tender Document to help the Contractor to make up the tender is not guaranteed. The Contractor shall be deemed to have examined the Contract Documents, to have generally obtained his own information in all matters whatsoever that might affect the carrying out of the works at the scheduled rates and to have satisfied himself to the sufficiency of his offe | We would request you to kindly delete the underlined statement as it implies Employer not being responsible for contents /specifications of this tender. | Contractual | The terms and conditions in the tender document shall prevail.
78 | M/s Vikram Solar | GCC | 93 | 19.1 | 19. Force Majeure A ‘Force Majeure’ means any event or circumstance or combination of events those stated below that wholly or partly prevents or unavoidably delays an Affected Party in the performance of its obligations under this Agreement, but only if and to the extent that such events or circumstances are not within the reasonable control, directly or indirectly, of the Affected Party and could not have been avoided if the Affected Party had taken reasonable care or complied with Prudent Utility Practices: | we would request you to include pandemic/ COVID 19 as well | Contractual | Kindly refer Amedment -1
79 | M/s Vikram Solar | GCC | 93 | 19.2 | 19.2 Force Majeure Exclusions • Strikes at the facilities of the Contractor / Affected Party | Pls modify as under: • Strikes at the facilities of the Contractor / Affected Party except for Industry wide strike. | Contractual | The terms and conditions in the tender document shall prevail.
80 | M/s Vikram Solar | GCC | 95 | 20.1 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities | We understand that the delay LD is not applicable on O&M portion of contract. Pls confirm. | Finance | This LD will be applicable for delay in Time for Commissioning and not valid for O&M contract. Please refer to Technical Section for details on LD for O&M period.
81 | M/s Vikram Solar | GCC | 95 | 20.1 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities. The Owner may, without prejudice to any other method of recovery, deduct the amount of such damages from any amount due or to become due to the Contractor. The payment or deduction of such damages shall not relieve the Contractor from his obligation to complete the Works, or from any other of his obligations and liabilities under the Contract. Once the maximum limit is reached, Owner may consider the termination of contract and/or shall have the discretion of getting executed the work from the Contractor with the maximum limit of Liquidated damages. Any such recovery on account of the Liquidated damages can be done from the running bills of the Contractor by Owner. | Meaning of underlined portion i.e.recourse susbequent to Delay LD ceiling is breached needs clarity. The statement is not clear as the stated words i.e. "or shall have the discretion of getting executed the work from the Contractor with the maximum limit of Liquidated damages" doesn't reflects appropriate meaning. Request you to kindly review. | Contractual | Kindly refer Amedment -1
82 | M/s Vikram Solar | - |  | 25.2 | 25.2 Termination for Contractor’s Default 25.2.1 Neither the Owner or PMC nor the Contractor may assign the Contract or any part thereof, or any right, benefit, obligation, or interest therein or thereunder, to any third party without the express prior written consent of the other Party, which consent shall not be unreasonably withheld, except that the Contractor shall be entitled to assign any monies due and payable to it or that may become due and payable to it under the Contract, either absolutely or by way of charge. | The said paragraph seems to be out of contexr w.r.t. the applicable clause heading. | Contractual | The mentioned clause is in reference to the "Assignment" of works.
83 | M/s Vikram Solar | - |  | 25.2.5 | 25.2.5 The Owner may enter upon the Site, expel the Contractor, and complete the Facilities itself or by employing any third Party. The Owner may, to the exclusion of any right of the Contractor over the same, take over and use with the payment of a fair rental rate to the Contractor, with all the maintenance costs to the account of the Owner and with an indemnification by the Ownerfor all liability including damage or injury to persons arising out of the Owner’s use of such equipment, any Contractor’s Equipment owned by the Contractor and on the Site in connection with the Facilities for such reasonable period as the Owner considers expedient for the supply and installation of the Facilitie | Please modify as under: 25.2.5 The Owner may enter upon the Site, expel the Contractor, and complete the Facilities itself or by employing any third Party. The Owner may, subject to the exclusion of any right of the Contractor over the same, take over and use with the payment of a fair rental rate to the Contractor, with all the maintenance costs to the account of the Owner and with an indemnification by the Owner to Contractor for all liability including damage or injury to persons arising out of the Owner’s use of such equipment, any Contractor’s Equipment owned by the Contractor and on the Site in connection with the Facilities for such reasonable period as the Owner considers expedient for the supply and installation of the Facilities | Contractual | The terms and conditions in the tender document shall prevail.
84 | M/s Vikram Solar | GCC | 103 | 27.1 | 27.1 The Contractor shall not be entitled to any increase on the price or any other right or claim whatsoever by reason of any representation, explanation statement or alleged representation, promise or guarantees given or alleged to have been given to him by any person. | We under stand that any written clarifications /statements/amendments issued by SECI (PMC) are admissible for contractual claims ,as applicable. Request you to kindly confirm as this clause dilutes such obligation of SECI. | Contractual | The subject tender is Lumpsum (LS) Turnkey Contract wherein any representation related to price escalation post award is not admissible.
85 | M/s Vikram Solar | GCC | 110 | 38.2 | 38. Delays by PMC/ Owner or his Authorized representatives 38.2 No adjustment in Contract Price shall be allowed for reasons of such delays and extensions granted except as provided in Tender Document, where the PMC/ Owner reserves the right to seek indulgence of Contractor to maintain the agreed Time Schedule of Completion. In such an event the Contractor shall be obliged for working by Contractor's personnel for additional time beyond stipulated working hours as also Sundays and Holidays and achieve the completion date/interim targets. | We would request you to permit contract price adjustment incidental to reasons associated with delays inflicted upon by PMC/Owner. Such specified provisions shall eventually be a non viable finnacial risk for Contractor for the raesons not attributable to him. | Finance | The terms and conditions in the tender document shall prevail.
86 | M/s Vikram Solar | GCC | 117 | 51.1 | 51. Change in Laws and Regulations However, these adjustments would be restricted to direct transactions between the PMC and Contractor and Bought out items (dispatched directly from sub vendor's works to Site). These adjustments shall not be applicable on procurement of raw materials, intermediary components and intermediary services etc. by the Contractor. | Pls confirm if transactions are happening between PMC and Contractor or Owner and Contractor? | Finance | The transactions are between Owner and Contractor.
87 | M/s Vikram Solar | GCC | 117 | 51.1 | 51.1 If, after the date seven (7) days prior to the date of Bid submission, in the country where the Site is located, any law, regulation, ordinance, order or by-law having the force of law is enacted, promulgated, abrogated or changed (which shall be deemed to include any change in interpretation or application by the competent authorities) that subsequently affects the costs and expenses of the Contractor and/or the Time for Completion, the Contract Price shall be correspondingly increased or decreased, and/or the Time for Completion shall be reasonably adjusted to the extent that the Contractor has thereby been affected in the Performance of any of its obligations under the Contract. Contractor shall promptly and within 15 days of such enactment coming into force, forward relevant supporting documents to Owner | There seems to be duplication in provisions of Change in Law as is evident from the referred clauses , please confirm which one will supercede. | Contractual | Kindly refer Amedment -1
88 | M/s Vikram Solar | GCC | 118 | 51.1 | The term Change in Law shall refer to the occurrence of any of the following events pertaining to this project only after the date seven (7) days prior to the date of Bid submission, including (i) the enactment of any new law; or (ii) an amendment, modification or repeal of an existing law; or (iii) any change in the rates f any Taxes including any duties and cess or introduction of any new tax made applicable for setting up the project. |  | Contractual | Kindly refer Amedment -1
89 | M/s Vikram Solar | GCC | 119 | 53.3 | Wherever references are made in the Contract to codes and standards in accordance with which the Contract shall be executed, the edition or the revised version of such codes and standards current at the date of bid submission shall apply unless otherwise specified. | We understand that Change in Codes & Standards during execution is a part of Change in Law | Contractual | No.
90 | M/s Vikram Solar | GCC | 127 | 70 | 70.1 i) Subject to the provisions of sub-para (ii) of this clause, the Contractor shall, if ordered in writing by the Engineer-in-Charge/Project Manager, or his representative, temporarily suspend the Worksor any part thereof for such written order, proceed with the Work therein ordered to be suspended until, he shall have received a written order to proceed therewith. The Contractor shall not be entitled to claim compensation for any loss or damage sustained by him by reason of temporary suspension of the Works aforesaid. However, suitable time extension may be considered at the sole discretion of the owner. ii) In case of suspensions of entire Work, ordered in writing by Engineer-in-Charge/Project Manager, for a period of more than 03 (Three) months, the Contractor shall have the option to terminate the Contract | We would request owner to kindly compensate for costs incidental to such suspension of works. Given the fixed price nature of this tender, such 3 months suspension without financial compensation shall cause a a serious loss to the Contractor. | Finance
91 | M/s Vikram Solar | GCC |  |  | Above mentioned Arbitration clause will be applicable for the Disputes where the amount of claim is less than or equal to INR 1Crore (Indian Rupees One Crore only). For the cases of disputes where the amount of claim is more than INR 1 Crore (Indian Rupees One Crore), such disputes will be settled through commercial Courts established under the Commercial Courts, Commercial Division and Commercial Appellate divisions of High Courts act, 2015 | We would request to enhance the ceiling amount from INR 1 crs to 25 crs | Finance | The terms and conditions in the tender document shall prevail.
92 | M/s Vikram Solar | SCC | 159 | 10 | Replace the existing clause by following: In the matter of connectivity of Plant to DISCOM’s substation, the Owner will take the necessary connectivity permission, however, all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc. are to be taken by the Contractor. All the required fees including statutory fees, Supervision charges etc. shall be paid / born by the contractor. | 1. We understand that Connectivity permission & Bay allocation are interlinked. Hence Bay allocation shall be dealt by Owner only. Pls confirm. 2. Pls confirm that who shalll bear the annual charges levied by DISCOM for bay /transmisison line maintenance? 3. Incase the Contractor has to bear the he annual charges levied by DISCOM for bay /transmisison line maintenance , such charges shall be restricted till O&M tenure. Pls confirm. 4. Pls confirm if ROW is in Owner's scope for transmisison line? | Technical | 1. Permission for connectivity/bay allocation will be applied by the Owner. Howerver, the contractor will have to facilitate the approval process and deposit fees etc. 2. Maintenance of all the facilities including transmission cable/bay etc. which will be constructed within the scope of this contrct shall be in the scope of the contractor during construction and O&M period. 3. Yes - confirmed.
93 | M/s Vikram Solar | SCC | 159 | 13 | Interest bearing initial advance (OPTIONAL) of 10% of the Contract Value (i.e., total sum of all the Supply Contract) shall be released to the contractor upon receipt of unconditional acceptance of NOA, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final commissioning total amounting to | 1) We would request you to kindly permit interest free advance within the contractual delivery period for supplies. 2) we request DVC/ SECI to follow NTPC payment terms for providing Optimised project cost. | Finance | Kindly refer Amedment -1
94 | M/s Vikram Solar | TS | 210 | Annexure C | Liquidated Damages for Shortfall in PR For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service and absolute value of O & M Contract) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance. Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made. | 1)We would request you to release the payments against OAT. Contractor's liability on a/c of shortfall in OAT is aggregated to 10%+5%+3% i.e. 18% , which is extremely high. Hence we would request you to kindly consider ,susbequent to adjustment of performance LD , release of last 10% payment & not to encash the Performance BG. | Finance | The terms and conditions in the tender document shall prevail.
95 | M/s Vikram Solar | TS | 210 | Annexure C | Liquidated Damages for Shortfall in PR For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service and absolute value of O & M Contract) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance. Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made. | 1) We understand that O&M value is excluded from PR test related LD. | Finance | Kindly refer Amedment -1
96 | M/s Vikram Solar | TS | 277 | Annexure 2 | If the Contractor fails to achieve guaranteed annual CUF at the end of First Year, the Contractor shall pay compensation to the PMC (amount to be deducted from the Final Payment at the end of 1 year), an amount equal to the NPV of the estimated shortfall in cash flow resulting over the period of 25 years due to reduced Plant CUF, calculated at a tariff of Rs.3.5 per unit (kWh) and discount rate of 6.5%. The Contractor may take corrective action during the ensuing year to demonstrate the guaranteed CUF at the end of the 2nd year. In such case, the part of the Final Payment withheld by the PMC on account of Liquidated Damages shall be released and the CUF shall remain unchanged from the tender specifications.If the Contractor fails to demonstrate the guaranteed CUF at the end of 2nd Year as well, the CUF achieved at the end of First Year shall be fixed as the new Guaranteed CUF for the remaining period of this Contract. | We understand that in case the CUF guarantee in 1st year is not met, the amount retained as LD after 1st year ( considering 25 years of shortfall) shall be withheld.Further the CUF shortfall LD as applicable for subsequent years of O&M shall be adjusted from the said witheld amount. After the completion of O&M the balance amount shall be retained by Owner. Kindly confirm. | Finance | In case CUF is revised at the end of second year as per this clause, LD for subsequent years shall be based on the revised CUF.
97 | M/s Vikram Solar | - | 28.5 | TS Page 133 of 146 | The floating system shall consist of multiple modular floating units/platforms and connected to the ground using anchoring and mooring system. However, the float unit shall have minimum material thickness of 3 mm, with moisture retention of less than 5% | Request to consider avg 3 mm material thickness of floats. Kindly confirm | Technical | Kindly refer Amedment -1
98 | M/s Vikram Solar | - | 28.9 | TS Page 133 of 146 | The floats may be filled with virgin expanded polystyrene foam to increase the strength of the float and to serve as backup floatation system. | Foam filled floats are ruled out in the market, So No foam filled in floats. Kindly Confirm. | Technical | Foam filling is not mandatory; it shall be as per the design of the floats.
99 | M/s Vikram Solar | - | 28.11 | TS Page 134 of 146 | The materials used for manufacturing the floating unit shall be tested at ILAC member signatory accredited testing laboratory for ensuring the suitability of the material for use in aqueous applications. | Float material tested at the CIPET laboratory. Kindly confirm | Technical | NABL is Mutual Recognition Arrangement (MRA) signatory to ILAC for Testing and Calibration as per ISO/IEC 17025. Hence, all the NABL accredited laboratories are eligible to perform testing.
100 | M/s Vikram Solar | - | 28.12 | TS Page 134 of 146 | All the modules shall be accessible for maintenance once multiple floating units are connected together. | Vikram is considering 4 in a row arrangement. DVC to confirm the same or suggest changes, if any. | Technical | The terms and conditions in the tender document shall prevail.
101 | M/s Vikram Solar | - | 28.3.1 | TS Page 133 of 146 | ASTM D 2565 - Standard Practice for Xenon-Arc Exposure of Plastics Intended for Outdoor Applications. More than 50% of its original break elongation after 10,000 hours exposure | VSL would provide report for 3380 hours of exposure. Kindly confirm | Technical | Kindly refer Amedment -1
102 | M/s Vikram Solar | - | 28.3.1 | TS Page 132 of 146 | ASTM D790 - Standard Test Methods for Flexural Properties of Unreinforced and Reinforced Plastics and Electrical Insulating Materials Secant Flexural Modulus at 2% Strain > 1000 Mpa | Result should be changed to Secant Flexural Modulus at 2% Strain > 750 Mpa. Kindly confirm | Technical | Kindly refer Amedment -1
103 | M/s Vikram Solar | - | 28.3.1 | TS Page 133 of 146 | ASTM D 638 - Standard Test Method for Tensile Properties of Plastics Tensile Strength at Yield > 27 Mpa | Result should be changed to Tensile Strength at Yield > 20 Mpa .Kindly confirm | Technical | Kindly refer Amedment -1
104 | M/s Vikram Solar | - | 28.3.1 | TS Page 133 of 146 | ASTM D695 - Standard Test Method for Compressive Properties of Rigid Plastics Compressive Stress at Yield > 10 Mpa | Result should be changed to Compressive Stress at Yield > 6 Mpa. Kindly confirm | Technical | Kindly refer Amedment -1
105 | M/s Vikram Solar | - |  |  | Soil Test report | Kindly provide us the Soil test report for Koderma and Mejia sites | Technical | Not available.
106 | M/s Vikram Solar | - |  |  | Anchoring and mooring system | Provision for installing concrete blocks at periphery of each reservoir for each site for anchoring and mooring system. Kindly confirm | Technical | The terms and conditions in the tender document shall prevail.
107 | M/s Vikram Solar | - |  |  |  | Kindly share Autocad drawings of each reservoir for each site for exact estimation.If available | Technical | Please refer updated Tender Drawings
108 | M/s Vikram Solar | - | 28.16 | TS Page 134 of 146 | The design of complete system comprising of Floating unit and anchoring & mooring system, shall be vetted by IITs or NIOT, Chennai and submit it for PMC’s approval during detailed engineering. | Certification from an internationally accredited laboratory/IRS(Indian Register of Shipping will be provided . Kindly confirm | Technical | Kindly refer Amedment -1
109 | M/s Vikram Solar | - | 6.16 | SOW Page 14 of 19 | Construction of transmission infrastructure at required voltage level from plant take off point to the designated substation including right of way (ROW) and construction of bay at designated substation as per DVC/CEA requirements/procedures | If any ROW is required for transmission or any other purpose , the same will be taken by DVC. And supoer vision charges for bay and transformer | Technical | Project location and entire route for power evacuation is within the DVC Project area. Hence, no ROW issue is envisaged
110 | M/s Vikram Solar | - | 3.6 | TS Page 16 of 146 | In case of string Inverters, average voltage drop (from PV module to string inverter) shall be limited to 0.5% of the rated voltage drop. | Can we consider string Inverters, average voltage drop (from PV module to string inverter) shall be limited to 1% of the rated voltage drop. Kindly confirm | Technical | The terms and conditions in the tender document shall prevail.
111 | M/s Vikram Solar | - | 1.1 Standards and Codes | TS Page 10 of 146 | IEC 61215-1-2:2016 Ed.1 | Not Applicable . Kindly confirm | Technical | It has been written specifically that the compliance shall be required only if the standard is applicable. IEC 61215-1-2:2016 Ed.1 is not applicable.
112 | M/s Vikram Solar | - |  | TS Page 10 of 146 | 2. PV Modules should be listed in the ALMM, as per MNRE Approved Models and Manufacturers of Solar Photovoltaic Modules (Requirements for Compulsory Registration) Order, 2019 | please consider subsequent amendments/incormartions. | Technical | Please refer the clause. It has been specifically mentioned that subsequent amendments are considered.
113 | M/s Vikram Solar | - | 1.3.2 | TS Page 11 of 146 | Gel content > 70% | Gel content > 60% . Kindly confirm | Technical | The terms and conditions in the tender document shall prevail.
114 | M/s Vikram Solar | - | 1.3.4 | TS Page 11 of 146 | The anodization thickness shall not be less than 15 micron. | The average anodization thickness shall not be less than 15 micron. Kindly confirm | Technical | The terms and conditions in the tender document shall prevail.
115 | M/s Vikram Solar | - | 1.3.6 | TS Page 12 of 146 | Each PV Module shall be provided a bar code which is embedded inside the module lamination | Barcode will be pasted outside of module as per MNRE standard. Kindly confirm | Technical | Kindly refer Amedment -1
116 | M/s Vikram Solar | - | C | 276/284 | Solar data GHI from Solar GIS | Please share the annual GHI data to bring all bidders at par. | Technical | Choosing the GHI data source is the independent decision of the biddder. SECI provides Radiation correction factor (RCF) based on the Refernce GHI mentioned in the O&M Contract. The same has been amended for better clarification.
117 | M/s Vikram Solar | - | 1 | 4/284 | Performance Parameters (PR & CUF) at plant S/s | For clarity purpose pelase clarify Plant S/s here means excluding TL | Technical | Yes
118 | M/s Vikram Solar | - | 1 | 6/284 | Usable area reserviior | Please mark the usable area of the reservior for plant design | Technical | The complete reservoir area is allocated for Solar Plant installation and the Contractor upon in his own can optimize and select the usable area of the reservoir for plant design.
119 | M/s Vikram Solar | - | 1 | 6/284 | The Site is within premises of DVC | If the site is within the Plant premises, then security person may not be required, please confirm | Contractual | Yes, the site is within the DVC premises. However, the contractor needs to provide proper watch and ward facility in consultation with DVC so that the manpower for such task is optimized.
120 | M/s Vikram Solar | - | 1.2 | 129/284 | This excludes design, supply and installation of Galvanised 220 kV and 132 kV Transmission Line towers, Tower extensions & accessories and 11 kV, 22kV & 33 kV transmission poles & accessories which shall be designed following latest guidelines of respective SEB (State electricity board) and got approved before execution. In absence of SEB/ STU guidelines REC (Rural electrification corporation) standards may be followed. Poles at corner with angle > 100 shall be provided with 4-pole structure or lattice tower. Use of PCC spun poles is not acceptable. Approved copies of these designs & drawings shall be submitted to the PMC for reference and record. | please review this scope if this is related to this tender | Technical | Technical Specifications is a general document. Please refer special technical specification. All works shall be executed as per Technical Specifications given in Section VII-B. Section VII-C lays down Special Technical Specifications with reference to site specific design requirements. However, in case of any conflict in requirements between Section VII-C and Section VII-B, Section VII-C shall have the precedence.
121 | M/s Vikram Solar | - | - | - | Estimate of the project including tax and O&M | Please share the tentative estimate of the Project including tax and O&M | Finance | Estimated project cost is for internal reference of SECI and DVC only. Can’t be shared with the bidders.
122 | M/s Vikram Solar | - | - | - | Grid Limitation | Please confirm if there is any Grid limitations on AC capacity of the project | Technical | No.
123 | M/s Vikram Solar | - | - | - | Cable tray | There are few existing cable trays at the site, please confirm of existing cable trays can be used for this project. | Technical | Power & communication cable laying for the solar project will be through existing cable tray/trench (whereever anvailable) and through newly constructed (under scope of this contract) cable tray/trench as per requirment of the project and NIT specification. Bidders are required to asses site requirment by visiting the project sites.
124 | M/s Vikram Solar | - | - | - | Bay Construction | Please confirm if bays are required to be constructed all the 3 sites. | Technical | Yes
125 | M/s Vikram Solar | - | - | - | project connectivitry approvals | Please confirm if the bidders has to take the grid connectivity approval or DVC has already taken the approvals for all 3 sites. | Technical | Permission for connectivity/bay allocation will be applied by the Owner. Howerver, the contractor will have to facilitate the approval process and deposit fees etc.
126 | M/s Vikram Solar | SECTION-VII: TS-Civil | - | - | Drawing | For RTPS site, MDDL mentioned is 144 and the reservoir-1 bed has different levels,viz,144,145.7,149.7 and reservoir-2 bed has different levels,viz,144,146.7. So pls confirm whether we have to consider only 144 bed level area for floating system or what. Kindly confirm | Technical | 152 m may be consider as MDDL for RTPS site.
127 | M/s Solarworld Energy | SECTION – III- BDS | - | 1.3.1 | For participation as an EPC Bidder under Route I: In case the bidder is a subsidiary of a holding company, financial eligibility criteria referred to in clause 1.3 above shall be of that subsidiary company only (i.e. excluding its holding company). | Request you to please allow to consider Holding Company Financial Eligibility Criteria to meet Minimum Average Turnover. Same is been considered in NTPC/NHPC/SJVN by taking undertaking from Holding Company. It will help in increasing competition and also cover the financial risk of Employee | Contractual | The terms and conditions in the tender document shall prevail.

## Amendment-1
Tender No : SECI/C&P/PMC/11/0003/2021-22
Tender for Design, Engineering, Supply, Construction, Erection, Testing, commissioning and O&M of 22 MW (AC) OB Dump based Solar PV Power Plant at RG OC 1
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | SECTION - I Invitation for Bids | 4 of 11 | 4 | The provisions as contained in the O.M. dated 10.03.2021 issued by MNRE on the subject “Approved Models and Manufacturers of Solar Photovoltaic Modules (requirement of compulsory registration) Order, 2019-Implementation-Reg.” and its subsequent amendments and clarifications, shall be applicable for this tender. The Cells and Modules used in this tender shall be sourced only from the Models and Manufacturers included in the List-I (Solar PV Modules) of ALMM Order, Annexure-I of the OM, issued by MNRE on 10th March 2021 which will be updated by MNRE from time to time. The modules to be supplied under this tender, shall be from the List-I of the ALMM order applicable on the date of invoicing of such modules. Bidders shall also provide a disclosure regarding that they are aware of binding provisions of the ALMM order and the list(s) thereunder, while quoting for the tender. | The provisions as contained in the O.M. dated 10.03.2021 issued by MNRE on the subject “Approved Models and Manufacturers of Solar Photovoltaic Modules (requirement of compulsory registration) Order, 2019-Implementation-Reg.” and its subsequent amendments and clarifications, shall be applicable for this tender. The Modules used in this tender shall be sourced only from the Models and Manufacturers included in the List-I (Solar PV Modules) of ALMM Order, Annexure-I of the OM, issued by MNRE on 10th March 2021 which will be updated by MNRE from time to time. The modules to be supplied under this tender, shall be from the List-I of the ALMM order applicable on the date of invoicing of such modules. Bidders shall also provide a disclosure regarding that they are aware of binding provisions of the ALMM order and the list(s) thereunder, while quoting for the tender.
2 | Annexure to BDS Qualifying Requirements | 3 of 7 | 1.2 | Route I IA. The bidder should have experience in EPC execution of Ground mounted Solar Projects on Turnkey basis including Design, Supply (Supply of Modules & Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), Installation and Commissioning of Grid connected Solar PV Power Plant of cumulative Capacity not less than 15 (Fifteen) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. AND IB. Out of the above, the bidder should have experience in EPC execution of Ground mounted Solar Projects on Turnkey basis including Design, supply (Supply of Modules & Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), installation & commissioning of at least 02 (Two) Grid connected Solar PV Power Plant Projects having an individual capacity of 3 (Three) MW or above in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. OR Route II IIA. The bidder should have experience in execution of Ground mounted Solar Projects as a Developer of Grid-connected Solar PV Power Plant(s) of cumulative Capacity not less than 15 (Fifteen) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. AND IIB. Out of the above, the bidder should have experience in execution of Ground mounted Solar Projects as a Developer of at least 02 (Two) Grid connected Solar PV Power Plant Projects having an individual capacity of 3 (Three) MW or above in last seven Financial years and till last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. | Route I IA. The bidder should have experience in EPC execution of Floating Solar or Ground mounted Solar Projects on Turnkey basis including Design, Supply (Supply of Modules & Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), Installation and Commissioning of Grid connected Solar PV Power Plant of cumulative Capacity not less than 15 (Fifteen) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. AND IB. Out of the above, the bidder should have experience in EPC execution of Floating Solar or Ground mounted Solar Projects on Turnkey basis including Design, supply (Supply of Modules & Inverters can be inclusive or exclusive in the bidder’s scope in the past experience), installation & commissioning of at least 02 (Two) Grid connected Solar PV Power Plant Projects having an individual capacity of 3 (Three) MW or above in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. OR Route II IIA. The bidder should have experience in execution of Floating Solar or Ground mounted Solar Projects as a Developer of Grid-connected Solar PV Power Plant(s) of cumulative Capacity not less than 15 (Fifteen) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. AND IIB. Out of the above, the bidder should have experience in execution of Floating Solar or Ground mounted Solar Projects as a Developer of at least 02 (Two) Grid connected Solar PV Power Plant Projects having an individual capacity of 3 (Three) MW or above in last seven Financial years and till last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission.
3 | Annexure to BDS Qualifying Requirements | 4 of 7 | 1.3 | The bidder should have a minimum Working Capital of INR 50,27,00,000/- (Indian Rupees Fifty crores twenty seven lakhs only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 50,27,00,000/- (Indian Rupees Fifty crores twenty seven lakhs only) to meet the working Capital requirement of this particular Project. | The bidder should have a minimum Working Capital of INR 33,51,00,000/- (Indian Rupees Thirty Three crores fifty one lakhs only) as per the last audited financial statement. If the bidder’s working capital is inadequate, the bidder should supplement this with a letter from the bidder’s bank, having net worth not less than INR 500 Crores, confirming availability of the line of credit for more than or equal to INR 33,51,00,000/- (Indian Rupees Thirty Three crores fifty one lakhs only) to meet the working Capital requirement of this particular Project.
4 | Annexure to BDS Qualifying Requirements | 5 of 7 | 1.4.2 | There can be a maximum of 03 (Three) partners/members in a JV/Consortium. The Lead partner/member of the JV/Consortium shall meet individually not less than 50% of minimum Financial Eligibility Conditions (MAAT & Working Capital) given at para 1.3 above. However, all the JV/Consortium partners/members must meet collectively 100% Financial Eligibility Conditions given at para 1.3 above. Herein, apart from the Lead partner/member, a minimum of 25% Financial eligibility should be met individually by all other partners/members of the JV/Consortium. | There can be a maximum of 03 (Three) partners/members in a JV/Consortium. The Lead partner/member of the JV/Consortium shall meet individually not less than 50% of minimum Financial Eligibility Conditions (MAAT & Working Capital) given at para 1.3 above. However, all the JV/Consortium partners/members must meet collectively 100% Financial Eligibility Conditions given at para 1.3 above.
5 | Section - IV General Conditions of Contract | 21 of 81 | 19.1 | "A ‘Force Majeure’ means any event or circumstance or combination of events those stated below that wholly or partly prevents or unavoidably delays an Affected Party in the performance of its obligations under this Agreement, but only if and to the extent that such events or circumstances are not within the reasonable control, directly or indirectly, of the Affected Party and could not have been avoided if the Affected Party had taken reasonable care or complied with Prudent Utility Practices: • Act of God, including, but not limited to lightning, fire not caused by Suppliers’ negligence and explosion (to the extent originating from a source external to the site), earthquake, volcanic eruption, landslide, unprecedented flood, cyclone, typhoon, or tornado. {Only if it is declared / notified by the competent state / central authority / agency (as applicable)}, • Any act of war (whether declared or undeclared), invasion, armed conflict or act of foreign enemy, blockade, embargo, revolution, riot, insurrection, terrorist or military action, quarantine. • Radioactive contamination or ionizing radiation originating from a source in India or resulting from another Force Majeure Event mentioned above. " | A ‘Force Majeure’ means any event or circumstance or combination of events those stated below that wholly or partly prevents or unavoidably delays an Affected Party in the performance of its obligations under this Agreement, but only if and to the extent that such events or circumstances are not within the reasonable control, directly or indirectly, of the Affected Party and could not have been avoided if the Affected Party had taken reasonable care or complied with Prudent Utility Practices: • Act of God, including, but not limited to lightning, fire not caused by Suppliers’ negligence and explosion (to the extent originating from a source external to the site), earthquake, volcanic eruption, landslide, unprecedented flood, cyclone, typhoon, tornado, pandemic and quarantine. {Only if it is declared / notified by the competent state / central authority / agency (as applicable)}, • Any act of war (whether declared or undeclared), invasion, armed conflict or act of foreign enemy, blockade, embargo, revolution, riot, insurrection, terrorist or military action. • Radioactive contamination or ionizing radiation originating from a source in India or resulting from another Force Majeure Event mentioned above.
6 | Section - IV General Conditions of Contract | 23 of 81 | 20.1 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities. The Owner may, without prejudice to any other method of recovery, deduct the amount of such damages from any amount due or to become due to the Contractor. The payment or deduction of such damages shall not relieve the Contractor from his obligation to complete the Works, or from any other of his obligations and liabilities under the Contract. Once the maximum limit is reached, Owner may consider the termination of contract and/or shall have the discretion of getting executed the work from the Contractor with the maximum limit of Liquidated damages. Any such recovery on account of the Liquidated damages can be done from the running bills of the Contractor by Owner. | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning or any extension thereof of Plant facilities in accordance with timelines as mentioned under the SCC, then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities. The Owner may, without prejudice to any other method of recovery, deduct the amount of such damages from any amount due or to become due to the Contractor. The payment or deduction of such damages shall not relieve the Contractor from his obligation to complete the Works, or from any other of his obligations and liabilities under the Contract. Owner may consider the termination of contract and/or shall have the discretion of getting executed the work from the Contractor once the maximum limit of LD is reached. Any such recovery on account of the Liquidated damages can be done from the running bills of the Contractor by Owner.
7 | Section - IV General Conditions of Contract | 45 of 81 | 51.1 | If, after the date seven (7) days prior to the date of Bid submission, in the country where the Site is located, any law, regulation, ordinance, order or by-law having the force of law is enacted, promulgated, abrogated or changed (which shall be deemed to include any change in interpretation or application by the competent authorities) that subsequently affects the costs and expenses of the Contractor and/or the Time for Completion, the Contract Price shall be correspondingly increased or decreased, and/or the Time for Completion shall be reasonably adjusted to the extent that the Contractor has thereby been affected in the Performance of any of its obligations under the Contract. Contractor shall promptly and within 15 days of such enactment coming into force, forward relevant supporting documents to Owner. However, these adjustments would be restricted to direct transactions between the PMC and Contractor and Bought out items (dispatched directly from sub vendor's works to Site). These adjustments shall not be applicable on procurement of raw materials, intermediary components and intermediary services etc. by the Contractor. Notwithstanding the foregoing, such additional or reduced costs shall not be separately paid or credited if the same has already been accounted for in the price adjustment provisions where applicable. However, any increase in the rate of these taxes, duties and levies beyond the contractual completion period shall be to Contractor's account and any decrease shall be passed on to Owner. The term Change in Law shall refer to the occurrence of any of the following events pertaining to this project only after the date seven (7) days prior to the date of Bid submission, including (i) the enactment of any new law; or (ii) an amendment, modification or repeal of an existing law; or (iii) any change in the rates of any Taxes including any duties and cess or introduction of any new tax made applicable for setting up the project. However, Change in Law shall not include (i) any change in taxes on corporate income or (ii) any change in any withholding tax on income or dividends distributed to the shareholders of the Contractor, or (iii) any change on account of regulatory measures by the Appropriate Commission. | If, after the date seven (7) days prior to the date of Bid submission, in the country where the Site is located, any law, regulation, ordinance, order or by-law having the force of law is enacted, promulgated, abrogated or changed (which shall be deemed to include any change in interpretation or application by the competent authorities), including (i) the enactment of any new law; or (ii) an amendment, modification or repeal of an existing law; or (iii) any change in the rates of any Taxes including any duties and cess or introduction of any new tax made applicable for setting up the project that subsequently affects the costs and expenses of the Contractor and/or the Time for Completion, the Contract Price shall be correspondingly increased or decreased, and/or the Time for Completion shall be reasonably adjusted to the extent that the Contractor has thereby been affected in the Performance of any of its obligations under the Contract. Contractor shall promptly and within 15 days of such enactment coming into force, forward relevant supporting documents to Owner. However, these adjustments would be restricted to direct transactions between the PMC and Contractor and Bought out items (dispatched directly from sub vendor's works to Site). These adjustments shall not be applicable on procurement of raw materials, intermediary components and intermediary services etc. by the Contractor. Notwithstanding the foregoing, such additional or reduced costs shall not be separately paid or credited if the same has already been accounted for in the price adjustment provisions where applicable. However, any increase in the rate of these taxes, duties and levies beyond the contractual completion period shall be to Contractor's account and any decrease shall be passed on to Owner. However, Change in Law shall not include (i) any change in taxes on corporate income or (ii) any change in any withholding tax on income or dividends distributed to the shareholders of the Contractor, or (iii) any change on account of regulatory measures by the Appropriate Commission.
8 | Section - V Special Conditions of Contract | 2 of 9 | 3 | The Time for Commissioning for the cumulative capacity of 30 MW floating Solar PV Power Plant at 03 different sites along with other associated equipment as per this tender document in total shall be 12 (Twelve) Months from the Date of the Notification of Award NOA/LOA/LOI. Further Contractor is also to provide Operation & Maintenance Contract of Solar Photo Voltaic Plant for a period of 10 (Ten) years from the date of Operational Acceptance of the Plant. | The Time for Commissioning for the cumulative capacity of 30 MW floating Solar PV Power Plant at 03 different sites along with other associated equipment as per this tender document in total shall be 18 (Eighteen) Months from the Date of the Notification of Award NOA/LOA/LOI. Further Contractor is also to provide Operation & Maintenance Contract of Solar Photo Voltaic Plant for a period of 10 (Ten) years from the date of Operational Acceptance of the Plant.
9 | Section - V Special Conditions of Contract | 2 of 9 | 3
10 | Section - V Special Conditions of Contract | 5 of 9 | 9 | The Contract Performance Security against this Contract need to be furnished as mentioned below: 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 3% (Three percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 135 Months (12 Months Project commissioning period) + prescribed O & M Period, i.e., 120 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 135 months period. | The Contract Performance Security against this Contract need to be furnished as mentioned below: 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 3% (Three percent) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 141 Months (18 Months Project commissioning period) + prescribed O & M Period, i.e., 120 Months + 03 Months additional) from the date of its issuance. The successful bidder can submit Contract Performance Security with initial validity of 36 months and the same may be extended after every 36 months till completion of the total 141 months period.
11 | Section - V Special Conditions of Contract | 6 of 9 | 13 | i) Interest bearing initial advance (OPTIONAL) of 10% of the Contract Value (i.e., total sum of all the Supply Contract) shall be released to the contractor upon receipt of unconditional acceptance of NOA, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final commissioning total amounting to 110% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security. The annual interest rate shall be calculated based SBI one-year MCLR as applicable. ............ * In case the Interest-bearing initial advance (OPTIONAL) of 10% of the Contract Value is not availed by the contractor, then this 10% payment amount will be payable along with the point No A ii) along with the 70% payment milestone. | i) Interest free initial advance (OPTIONAL) of 10% of the Contract Value (i.e., total sum of all the Supply Contract) shall be released to the contractor upon receipt of unconditional acceptance of NOA, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final commissioning total amounting to 110% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security. ............ * In case the Interest free initial advance (OPTIONAL) of 10% of the Contract Value is not availed by the contractor, then this 10% payment amount will be payable along with the point No A ii) along with the 70% payment milestone.
12 | Scope of Works | 11 of 19 | 4.23 | "Weather monitoring station shall include but not be limited to the following:  Pyranometers – Two in Horizontal Plane for GHI and two in inclined plane for GTI – Minimum 4 (Four) Nos.  Ultrasonic Anemometer (wind speed and direction) – 2 (two) no.  Temperature Sensor (ambient and module surface) – 3 (three) nos.  Power source to the all sensors wherever required  Data Logger" | "Weather monitoring station shall include but not be limited to the following (will be provided for each site):  Pyranometers – Two in Horizontal Plane for GHI and two in inclined plane for GTI – Minimum 1 (One) Nos.  Ultrasonic Anemometer (wind speed and direction) – 1 (one) no.  Temperature Sensor (ambient and module surface) – 1 (one) nos.  Power source to the all sensors wherever required  Data Logger"
13 | Technical Specifications | 12 of 146 | 1.3.6 | Each PV Module shall be provided a bar code which is embedded inside the module lamination and must be able to withstand harsh environmental conditions. | Each PV Module shall be provided a bar code which is embedded either inside or outisde the module lamination and must be able to withstand harsh environmental conditions.
14 | Technical Specifications | 15 of 146 | 3.2 | Both solar and DC cables shall be marine grade cables complying with relevant standards | Void.
15 | Technical Specifications | 59 of 146 | 15.3.9 | Shall not require a static public IP address, at the plant for the purpose of remote access. | Shall require a static public IP address, at the plant for the purpose of remote access.
16 | Technical Specifications | 99 of 146 | 21.3.2 | Area. LUX Control Room and equipment rooms. 300 Office. 300 Battery & other rooms. 150 Internal. 4 Transformer yard/Switchyard. 20 H – pole and metering point. 10 | Area. LUX Control Room and equipment rooms. 300 Office. 300 Battery & other rooms. 150 Internal/Pheripheral Roads. 4 Transformer yard/Switchyard. 20 H – pole and metering point. 10
17 | Annexure C - PG Test Procedure | 10 of 10 | - | Liquidated Damages for Shortfall in PR For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service and absolute value of O & M Contract) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance. Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made. | Liquidated Damages for Shortfall in PR For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply & Service) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance. Security submitted by the contractor will be forfeited & payments linked to operational acceptance will not be made.
18 | Annexure:G Plant O&M :Annexure 2: Functional Gurantees | 39 | 1 | … Eac is the number of units recorded in the plant end ABT meter excluding auxiliary consumption, kWh … | … Eac is (Number of units recorded in the substation end ABT meter) - (Plant Auxiliary consumption), kWh …
19 | Annexure:G Plant O&M :Annexure 2: Functional Gurantees | 45 | 2.1 | In case of any deviation due to forecasting and scheduling error (above and below 15%), Contractor shall bear the cost/Penalty. | In case of any deviation due to forecasting and scheduling error , Contractor shall bear the cost/Penalty.
20 | Annexure:G Plant O&M :Annexure 2: Functional Gurantees | 38 | Annexure 2 | Reference Irradiation for the site = Long-term avg of SolarGIS data. The Measured Irraditation (GHImes) shall be recorded from the Pyranometer installed in horizontal plane at the site location (average in case of multiple pyranometers). The radiation data of the Pyranometer shall be compared with the Reference Irradiation mentioned above. The radiation data from the Plant Pyranometer shall be used for computation of CUF, except in case of any discrepancy (i.e. more than ± 10% variation from the Reference Radiation, GHIref), in which case the radiation data from SolarGIS database for the said period will be used for computation of CUF. Missing data (GHImes) from the Plant Pyranometer shall be substituted by average of GHI measured for the same period in the past three (3) days. The plant Pyranometer has to be under CCTV coverage. | Reference Irradiation for the site (taken from SolarGIS database) = 1796 KWh/m2 (Raghunathpur), 1769 KWh/m2 (Mejia), 1832 KWh/m2 (Koderma) The Measured Irraditation (GHImes) shall be recorded from the Pyranometer installed in horizontal plane at the site location (average in case of multiple pyranometers). The radiation data of the Pyranometer shall be compared with the Reference Irradiation mentioned above. The radiation data from the Plant Pyranometer shall be used for computation of CUF, except in case of any discrepancy (i.e. more than ± 10% variation from the Reference Radiation, GHIref), in which case the radiation data from SolarGIS database for the said period will be used for computation of CUF. Missing data (GHImes) from the Plant Pyranometer shall be substituted by average of GHI measured for the same period in the past three (3) days. The plant Pyranometer has to be under CCTV coverage.
21 | Special Technical Specifications | 2 of 3 | 1.5 | Design Considerations (New point added) | Probability of exceedence for the energy yield estimation shall be taken as P75 with minimum 5% variability.
22 | Special Technical Specifications | - | - | New Point | KML & DWG files are attached for all the sites.
23 | Technical Specifications | 132 of 146 | 28.3.1 | Re. Density > 0.9 Environmental Stress-Cracking Resistance, F50 (hrs.) > 500 Secant Flexural Modulus at 2% Strain > 1000 Mpa Tensile Strength at Yield > 27 Mpa Compressive Stress at Yield > 10 Mpa More than 50% of its original break elongation after 10,000 hours exposure | Re. Density > 0.9 Environmental Stress-Cracking Resistance: Zero Cracking for 48 Hours Secant Flexural Modulus at 2% Strain > 750 Mpa Tensile Strength at Yield > 22 Mpa Compressive Stress at Yield > 6 Mpa More than 85% of its original break elongation after 3,000 hours exposure (Cycle 4 of ASTM D 2565)
24 | Technical Specifications | 133 of 146 | 28.3.2 | For design of anchoring and mooring system, the following standards may referred (for guidance) – API RP 2SK, API Spec 2F, API RP 2I, API RP 2MIM & BS 6349-6. | For design of anchoring and mooring system, the following standards may be referred (for guidance) – API RP 2SK, API Spec 2F, API RP 2I, API RP 2MIM, BS 6349-6 & DNV-RP-C205. API RP 2A may be referred for floater strength verification, spreader bar design & pad eye design.
25 | Technical Specifications | 133 of 146 | 28.5 | The floating system shall consist of multiple modular floating units/platforms and connected to the ground using anchoring and mooring system. However, the float unit shall have minimum material thickness of 3 mm, with moisture retention of less than 5%. Floating system/platform shall be fenced with vacant floats to demarcate boundary. | The floating system shall consist of multiple modular floating units/platforms and connected to the ground using anchoring and mooring system. However, the float unit shall have average material thickness of 3 mm, with moisture retention of less than 5%. Floating system/platform shall be fenced with vacant floats to demarcate boundary.
26 | Technical Specifications | 134 of 146 | 28.16 | The design of complete system comprising of Floating unit and anchoring & mooring system, shall be vetted by IITs or NIOT, Chennai and submit it for PMC’s approval during detailed engineering | The design of complete system comprising of Floating unit and anchoring & mooring system, shall be vetted by IITs / NIOT, Chennai / Indian Register of Shipping and submit it for PMC’s approval during detailed engineering.
27 | Special Technical Specifications | 3 of 3 | 11 | Design of anchoring & mooring system shall be validated by IITs or NIOT and shall be submitted to PMC for approval. Maximum wave height and maximum water flow velocity shall be duly considered in the design of floating system. | Design of anchoring & mooring system shall be validated by IITs / NIOT, Chennai / Indian Register of Shipping and shall be submitted to PMC for approval. Maximum wave height and maximum water flow velocity shall be duly considered in the design of floating system.
28 | Special Technical Specifications |  | New Clause | - | Apart from the module cleaning arrangement envisaged under Cl 26 of Civil Section of Technical Specifications, the contractor may adopt to lay HDPE pipelines in arrays. Module cleaning manpower shall have access through boat or through reservoir banks/walkway. Reservoir water may be used for the purpose of module cleaning if it meets the quality requirements as per the Module Manufacturer and Cl 26.4 of Civil Section of Technical Specifications.
29 | Technical Specifications | 134 of 146 | 28.11 | The materials used for manufacturing the floating unit shall be tested at ILAC member signatory accredited testing laboratory for ensuring the suitability of the material for use in aqueous applications. | The materials used for manufacturing the floating unit shall be tested at CIPET/NABL accredited laboratory for ensuring the suitability of the material for use in aqueous applications.
30 | SECTION - VI Sample Forms and Format | 36 of 77 | Form F-15 | Form F-15 "Declaration regarding the fulfillment of Domestic Content Requirement Clause" | Void. This form is not required for this project.