## Pre Bid Queries
Design, Engineering, Supply, Construction, Erection, Testing, Commissioning including 5 Years Plant O&M of 2 MW (AC) Solar PV Power Plant with 01 MWh BESS at KAZA, Himachal Pradesh
Tender No : SECI/C&P/MI/00/0011/2022-23
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 | SECTION – VII | 4 | 1 Introduction | All the power cables coming out of Solar PV Plant and BESS shall be terminated at local Busbar at a common voltage level and only a single 22KV underground cable circuit shall be taken to the switchyard at Rongtong Power House. | The Rongtong SHP electrical SLD received, Please share te Rongtong power house SLD. | Technical | Already provided with the tender document as Annexure I
2 | SECTION – VII | 4 | 1 Introduction | Location 32°14'27.46"N, 78° 2'25.47"E Rangreek, Near Rong Tong Hydro Power Station, District – Lahaul and Spiti, Himachal Pradesh (Refer Annexure-A) | Please share .kmz file of the Solar PV Plant boundary along with Rongtong power house Switchyard location. | Technical | Please refer .dwg file provided along with tender documents as Annexure H
3 | SECTION – VII | 5 | 1 Introduction | Minimum values of PR and CUF of the plant after netting off the auxiliary consumption. PR : 0.80 & CUF : 21% | We understand that PR & CUF guarantee is connection point (i.e. Rongtong power house), Please clarify and confirm. | Technical | PR shall be measured at the Solar PV Feeder at the Solar PV and BESS pooling bus on the Plant end switchyard. CUF shall be measured at the interconnection point in the Rong Tong Power House.
4 | SECTION – VII | 5 | 1 Introduction | Minimum values of PR and CUF of the plant after netting off the auxiliary consumption. PR : 0.80 & CUF : 21% | We understand 21% is AC CUF, please confirm?. | Technical | Yes. Please refer Annexure G: Operations and Maintenance Agreement, Annexure 2: Functional Guarantees
5 | SECTION – VII | 6 | 3 Design and Engineering | Estimation of the plant generation based on Solar Radiation and other climatic conditions prevailing at site based on P75 values from Energy Yield Simulations. | We understand CUF guarantee is at P50, please confirm?. | Technical | As mentioned, P75 values have been used to estimate the plant generation. CUF guarantee is at P75.
6 | SECTION – VII | 25 | 3 Solar and DC Cables | In case of central inverters, average voltage drop in the cables (from PV Modules to PCU) shall be limited to 1.5 % of the rated voltage. | we propose, In case of central inverters, average voltage drop in the cables (from PV Modules to PCU) shall be limited to 2.5 % of the rated voltage. Please confirm?. | Technical | The terms and conditions in the tender document shall prevail.
7 | SECTION – VII | 28 | 4.2 Technical Requirements | The rated/ name plate AC capacity of the PCU shall be AC power output of the PCU at 25°C. | We understand Inverter AC Capacity and Overall Plant AC capacity to be designed at 25°C design ambient temperature. Please clarify and confirm?. | Technical | Yes. However, Equipment rating shall be suitably corrected for altitude.
8 | SECTION – VII | 32 | 5.2 Technical Requirements | VA Rating 1 MVA (2 nos.) | We propose single 2MVA Inverter duty transformer, Please clarify and confirm?. | Technical | The terms and conditions in the tender document shall prevail.
9 | SECTION – VII | 62 | 13.1 Optical Fibre Cables | The Contractor shall ensure that minimum 100% cores are kept as spare in all types of optical fibre cables. | we propose 50% spare cores, Please confirm?. | Technical | The terms and conditions in the tender document shall prevail.
10 | SECTION – VII | 62 | 12 Lightning Protection System | Lightning Protection Level for the entire plant shall be Level – III. | we propose Level-IV Lightning protection for PV array yard. Please confirm?. | Technical | The terms and conditions in the tender document shall prevail.
11 | SECTION – VII | 63 | 14 Communication Cable (Modbus) | Communication cable shall be laid through suitable HDPE ducts. | We Request to propose to install communication cables shall be laid openly as these are armoured cables, Please confirm?. | Technical | The terms and conditions in the tender document shall prevail.
12 | SECTION – VII | 73 | 19 CCTV Camera | (iv) Along the Plant Perimeter: Covering complete perimeter of Plant Area to capture all possible intrusion | We Request to exclude CCTV for perimeter, please confirm?. | Technical | The terms and conditions in the tender document shall prevail.
13 |  |  | General | Local content for Inverters | We Request to please clarify the local content clause on the String Inverters | Technical | Please refer S. No. 7 of Amendment 01
14 | TS | 78 of 136 | 10.10.2 | For estimation of design wind loads on purlins (Table 8 of IS 875- Part 3), WL(downward) and WL (upward) on modules (laid in the profile of mono slope canopy) shall be applied such that the centre of pressure should be at (0.3 × length of canopy) from windward end (for simplicity, the wind load distribution may be taken as triangular with max. value at windward end). Solidity ratio (∅) shall be taken as 0.5. | Interactions with prominent customers and technical forums have informed that the results of Wind tunnel testing on MMS structure are not in sync to the results obtained through MMS design done by Triangulation method and hence it is requested to review the same. | Technical | The terms and conditions in the tender document shall prevail.
15 | TS | 85 of 136 | 13.1 | The purlins shall be provided with min. following tie/sag rods or angles or channels:  1 no., in the mid of each span and shall connect all the purlin members  1 no., diagonal, at each corner in end spans | The introduction of so many sag angles increases the complexity of assembly at site. Please allow to place single sag angle/rod for purlins. | Technical | The terms and conditions in the tender document shall prevail.
16 | TS | 85 of 136 | 13.12 | The vertical diagonal bracing shall be provided in end spans and every alternate span of each unit (table) of MMS. | Bracing requirement should be as per requirement in Staad design. | Technical | The terms and conditions in the tender document shall prevail.
17 | TS | 86 of 136 | 13.21 | Two numbers of anti-theft fasteners of stainless steel on two diagonally opposite corners for each module shall be provided. All fasteners both for MMS connections and fixing of PV Module shall be adequately protected from atmosphere and weather prevailing in the area. | Anti theft fasteners are not recommended as it limits the replacement of PV module during O & M period. Also it does not ensure non-pilferage as the Modules can be still be stolen along with the purlins by opening the fastener connection between rafter and purlin.( Purlin will also provide support in carrying PV Modules.) | Technical | The terms and conditions in the tender document shall prevail.
18 | TS | 86 of 136 | 13.27 | In case the contractor proposes to extend the column leg to embed it in the pile/pedestal as an alternate fixing arrangement, the column member shall be extended for full depth of the pile (100mm cover at tip of the pile) with an end plate of min. 4mm thickness to be welded at the bottom of column leg. (However, for plants in coastal area or in case of marshy soil the column post shall be supported only with base secured to foundation through base plate and anchor bolt assembly and no embedment of column leg in foundation is permitted) | Welding end plate to Column shall delay Manufacturing of MMS Columns , and MMS Columns are the first items required at site. Instead Bolting of Cleats to the MMS-Column to be permitted. | Technical | Refer S. No. 2 of Amendment 01
19 | TS | 86 of 136 | 13.31 | The length of one unit (Table) of MMS shall not generally be more than 20m. | With 1500V System design we are providing 60 modules table in projects having length upto 30 M. Please permit. | Technical | The terms and conditions in the tender document shall prevail.
20 | TS | 87 of 136 | 13.36 | The purlin splice shall comprise of flange and web splice plates and splice design shall conform to Annexure-F of BIS:800. For simplicity in fabrication, the splice member may be of CFS channel section without lips (CU). There shall be min. four number of bolts on either sides of joints in web zones and one number of bolt on either side of joint in flange zones. | As per experience though the fabrication of C-Channel splice may be faster , however with the allowed tolerance in MMS Manufacturing it never fits at all the three faces of the purlin( two flange + one web) . In case of non-mating of purlin with purlin spice at all faces the effort of providing C-Channel with so many bolts is defeated. Even if tolerances are controlled in fabrication stage( will delay fabrication) assembly at site will delay overall execution. | Technical | Channel section to be used as splice member is suggestive. EPC contractor may propose separate splice plates for web and flanges.
21 | TS | 99 of 136 | 35.1.3 | Water used for drinking & PV module cleaning purpose shall generally be of potable quality and fit for cleaning the modules with TDS generally not more than 75 PPM. In case of higher salt contents, the water shall be thoroughly squeezed off to prevent salt deposition over module surface. However, water with TDS more than 200 PPM shall not be used directly for module cleaning without suitable treatment to control the TDS within acceptable limits. The water must be free from any grit and any physical contaminants that could damage the panel surface. | The recommended range for PPM from PV Module manufacturer is 300 to 400 ppm. Further, the PPM of cleaning water shall be as per recommendation of PV module manufacturer. | Technical | The terms and conditions in the tender document shall prevail.
22 | TS | 100 of 136 | 35.1.19 | Module cleaning procedure and pressure requirement at discharge point shall be as per the recommendation of PV module manufacturer. However, discharge pressure at outlet shall not be less than 5 kgf/cm2(0.5 MPa) | The pressure requirement at discharge point should be as per the recommendation of PV module manufacturer. 5 bar is unsafe and not recommended . It should be 2 bar as per PV Module manufacturer. | Technical | Refer S. No. 3 of Amendment 01
23 | SECTION – VII | 126 | E.3.Technical Specification of Battery Energy Storage System | BESS Availability -95% | If Grid is not available - same solar couping to grid will not be present. Same duration may not be considered as BESS non available duration. | Technical | Noted. Such period shall not be accounted for BESS availability
24 | SECTION – VII | 137 | Additional Control System Functions | The start and stop controls shall be as per DNP3 AN2011-001 standard specifications or IEC 61850. The control system shall use these controls for an orderly and safe shutdown, even in the absence of grid power. The control system shall also use these controls for an orderly startup sequence, which shall provide for a safe system reset from any standby or operating condition so that the unit goes through a normal startup sequence in the same way it would when being powered up after loss of power or being in a shutdown state | All controls may be modbus standards or DNP3 AN2011-001 standard specifications or IEC 61850. | Technical | The terms and conditions in the tender document shall prevail.
25 | General Query |  |  | BESS Charging /Discharging | BESS Charging /Discharging will be constant power mode or variable power mode | Technical | Charging in Variable Power Mode and Discharging in Constant Power Mode.
26 | General Query |  |  | BESS Coupling to Grid | Whether PCS output and PCU output may be paralleled at LV side of solar 22KV transformer | Technical | Solar PV and BESS Coupling shall be at the 22 kV Bus on the Plant Side.
27 | Annexure – C | 184 | 2.1.1 | IN PR Formula,𝐺𝑖,𝑘 is defined as Average irradiance measured at the Plane of Array (POA) at the commencement of time interval 𝜏𝑘 (kW/m2 ) ( average of all Pyranometers in various sites) | Please clarify the various site location for taking average of all Pyranometers in various sites | Technical | Please refer Annexure H for site topography. Location of Pyranometers shall be decided during detailed engineering review.
28 | Annexure – 2 | 263 |  | Capacity Utilization Factor (CUF) | Bidder understanding is ," Guarantee CUF is for overall pv plant including BESS" -Please confirm the same | Technical | Yes. CUF guarantee is for Overall Plant, including BESS. Please refer Clause C, Annexure 2 of Annexure G: Operations and Maintenance Agreement for CUF calculations. The ABT Meter at the Plant Interconnection point in the Rong Tong substation shall be considered for CUF calculations.
29 | Annexure – 2 | 263 |  |  | Please clarify the position of ABT meter, May please provide AC-SLD. | Technical | ABT Meter for CUF Guarantee shall be at the 22 kV Bus of the Interconnection point at the Rong Tong substation.
30 | Annexure – 2 | 264 |  | Reference Irradiation for the site = 1866 kWh/m2/year | Please provide month wise reference irradiation | Technical | As CUF guarantee is on annual basis, annual reference radiation has been provided.
31 | Section VII -B | 74 of 136 | 7.1 | The contractor shall design and construct storm water drainage network for smooth disposal of storm water from the plant to the nearest available drainage outlet. | Details of nearest drain to be mentioned: Type of drainage, Distance of nearest drainage from Site. | Technical | Please refer Annexure H.
32 | Section VII - B | 89 of 136 | 16.2.3.3 | Security room/ cabin shall be a pre-engineered & pre-fabricated structure. The walls and roof of the building shall be fabricated with double skin insulated sandwiched AlZn alloy coated high tensile steel metal panels (BMT- 0.5mm, Al-Zn alloy coating -150 GSM total on both sides). The insulation shall be of PUF with min. density 40 kg/ cum and adequate thickness | Minimum thickness of insulated puffed sheet for roof and wall to be mentioned. | Technical | Please refer S. No. 4 of Amendment 01
33 | General Query | - | - | - | Additional Reports required: 1. Preliminary Geo-Investigation / Soil Report 2. Topography report of the site. 3. Site Photographs | Technical | Please refer Annexure H. Site Photographs are uploaded on SECI website in the Tenders Section.
34 | Section VII-B | 71 of 136 | 5.3 | The contractor is responsible for making the site ready and easily approachable by clearing bushes, felling of trees (mandatory permissions/ licenses/ statutory clearances from competent authorities if required for cutting of trees, blasting or mining operations, disposal of waste material etc. shall be obtained by the contractor) | Bidder proposes Owner to arrange for necessary permission. | Technical | Noted.
35 | Section VII - A | 6 of 11 | 5.1.3 | Construction and erection of perimeter fence/ boundary wall and main/ security gate(s). | It is understood that boundary wall/ fencing under scope of bidder and encumbrance free land with fencing will be handed over to the bidder. | Technical | Noted.
36 | Section VII-B | 74 of 136 | 7.6 | The drainage scheme shall be designed considering the plant plot area and the surrounding catchment area contributing to the plant area drainage as per the topography | How much extra catchment area to be considered for design of new drain with the addition of existing drain outflow? | Technical | Shall be decided during detailed Engineering stage
37 | Section VII- B | 85 of 136 | 13.8 | Vertical deflection for Rafter and Purlin – Span/ 180 | Kindly allow for Span/150 for brittle cladding (PV modules) as per table -6 of IS-800 | Technical | The terms and conditions in the tender document shall prevail.
38 | Section VII- B | 80 of 136 | 12.2.1 | However, the min. dia of the pile shall be 300mm (min. 350 mm for column web depth more than 175 mm) and 1800mm respectively except when very hard strata/ rock (N>100) is encountered at a higher level, the pile shall be extended in to the hard strata minimum 1.5 times the diameter of the pile with total depth of the pile not less than 1200mm below cut-off level | Bidder proposes pile depth as per geotechnical report in place of minimum pile depth of 1800 mm | Technical | Please Refer S. No. 5 of Amendment 01
39 | Section VII - B | 117 of 136 | 5.5.1 | BESS - End of Life | Please provide details on the end of life of the BESS. Please clarify whether the dismantling and removal of the complete installed BESS at the end of life of BESS is in Bidder's or customer's scope. Scope clarity requested. | Technical | Please refer to Table 2: Supply-Specific Ratings and Requirements, Clause 3.1 for BESS Power and Energy ratings during the period of the Contract. Removal of the BESS at the end of Life is not in the Scope of the Contractor
40 | Section VII - A | 5 of 11 | 4.1.13 | Provision for specific data transfer to the State Load Dispatch Centre (SLDC) shall also be provided. | Bidder shall provide the SCADA and HMI interface at the site for monitoring/controlling the Site parameters. Further Bidder understands that for data transfer to the SLDC, dedicated communication link from site MCR to SLDC will be provided by Customer for data transmission. Also, any modifications, additional equipment required at SLDC shall be in Customer's scope. Please confirm. | Technical | Please refer Clause 4.1.13 of Scpe of Works. Provision of Data transfer to the SLDC, dedicated communication link from site MCR to SLDC for data transmission is in the Scope of the Bidder.
41 | Section VII - A | 6 of 11 | 4.1.24 | Design & construction of Transmission line/ cable from plant take off point to the designated substation including right of way (ROW). | Right of Way issues are time consuming and sometimes get into legal tangles which further leads to time loss and stoppages in contract execution. It is therefore requested that SECI obtains and passes on clear title of Land, free from all encumbrances and right of way to the Contractor on the date of NOA/LOA. Please accept. | Technical | Noted. Land, free from all encumbrances and right of way shall be handed over to the Contractor on the date of NOA/LOA.
42 | Section - IV (GCC) | 19 of 80 | 19 | Force Majeure | Bidder understands that snowfall shall be considered as Force Majeure condition, as snowfall will render it impossible to carry out any outdoor site activity. Please confirm. | Contractual | The terms and conditions in the tender document shall prevail. However the commissioning timeline has been kept 18 months keeping in mind the snowfall factor. Notice, however, is drawn to incentive Clause for commissioning of the Solar part of the Plant by 30 November 2023 under Clause 14 of SCC (Please refer Amendment 1 to the tender)
43 | Section I | IFB Page 8 of 10 | H | Tender Processing Fees | As per govt. notification MSME with valid Udyog Aadhaar/DIC certification are exempted form Tender Fee. Kindly allow in this tender also. We have observed in SECI's other tender No. (Ref:SECI/C&P/IPP/14/0005/22-23) Where such exemption is also given and same is expected for this tender. | Contractual | As per the MSME Notification 2012 any exemption for MSMEs including Tender processign Fee is not allowed for Works Contract. This tender being a Works Contract, no such exemption is allowed.
44 | Section I | IFB Page 8 of 10 | I | Earnest Money Deposit | As per govt. notification MSME with valid Udyog Aadhaar/DIC certification are exempted form Tender Fee. Kindly allow in this tender also. We have observed in SECI's other tender No. (Ref:SECI/C&P/IPP/14/0005/22-23) Where such exemption is also given and same is expected for this tender. | Contractual | As per the MSME Notification 2012 any exemption for MSMEs including EMD is not allowed for Works Contract. This tender being a Works Contract, no such exemption is allowed.
45 |  |  |  | Financial Bid | Financial bid format required | Finance | SOR Sheet has already been shared with the tender document.
46 | Section III | ANNEXURE TO BDS Page 4 of 7 | 1.3 | Financial Eligibility Conditions | Financial Eligibility conditions: Turnover of 30% of contract value shall be allowed . | Finance | The terms and conditions in the tender document shall prevail.
47 | Section V | SCC Page 7 of 10 | 13 | Schedule of Rates & Payments | Kindly explain the prorata basis of payment as we have three understanding while reading tender document: 1. 70% of prorata of total supply, 2. 70% of item wise supply 3. Supply may be completed in partial /lot wise and prorata bill will be cleared. | Contractual | Understanding (1) regarding the Payment Terms is correct.
48 | Section VII A | Page 3 of 11 | 1.1 | Project Particulars | PR of 80% is not possible. Whereas we can achieve 50% as per site condition. IEC 61724 is not possible in KAZA | Technical | Terms and Conditions of the tender Conditions shall prevail
49 | Section VII B | Page 8 of 136 | 1.2 | Photovoltaic Modules (Technical Requirements) | Temperature co-efficient of power will be described by module manufacturer before the supply | Technical | Ok
50 | Section VII B | Page 9 and 10 of 136 | 1.12,1.13 | Approval, Manufacturing and Inspection | Kindly suggest module manufacturer who can perform all test required in tender specs, as quantity is only 2 MW and your suggested tests and conditions will not accepted to ALMM approved manufacturer. | Technical | Terms and Conditions of the tender Conditions shall prevail
51 | Section VII B | Page 10 of 136 | 1.12 | Approval | No module manufacturer can provide Constructional Data Form (CDF)’s | Technical | CDF Data is available in PV Module Type Test Reports. Terms and Conditions of the tender Conditions shall prevail
52 | Section VII B | Page 9 of 136 | 1.12.1 | The EMPLOYER shall perform material inspection at the Manufacturer’s factory before the start of proposed manufacturing schedule. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification. | Not possible | Technical | Terms and Conditions of the tender Conditions shall prevail
53 | Section VII B | Page 10 of 136 | 1.13.1 | The Contractor shall inform the module manufacturing schedule to the EMPLOYER at least 7 (seven) working days before the start of proposed schedule | Not possible | Technical | Terms and Conditions of the tender Conditions shall prevail
54 | Section VII B | Page 13 of 136 | 3.5 | In case of central inverters, average voltage drop in the cables (from PV Modules to PCU) shall be limited to 1.5 % of the rated voltage. | Please allow 1.5% to 5% as per site conditions and subzero temperature (upto -40 Degree) as cables /conductor properties manufactured in India may not withstand harsh conditions. | Technical | Terms and Conditions of the tender Conditions shall prevail
55 | Section VII B | Page 19 of 136 | 5.2 | Technical Requirements of Inverter Transformer | Dry and oil type both transformer shall be allowed, as regular maintenance of Oil type is not feasible for Kaza. | Technical | Terms and Conditions of the tender Conditions shall prevail
56 | Section VII B | Page 70 of 136 | 5 | Area Grading and Land Development | Due to low resources of sand gravel and other items req. for area grading & levelling the suggested procedure may not be implemented. So we request you to use allow local traditional method for grading & levelling. We suggest you to separate this scope. | Technical | Terms and Conditions of the tender Conditions shall prevail
57 | Section VII B | Page 50 of 136 | 16 | SCADA/Monitoring | Data monitoring will be as per duration of availability of internet as site, Internet availability (GPRS/Broadband) is not very much reliable at site. | Technical | Terms and Conditions of the tender Conditions shall prevail
58 | Annexure -K | Page 1 of 10 |  | STANDARD SPECIFICATION FOR STATIC TEST ON PILE | Piling test is not possible | Technical | Terms and Conditions of the tender Conditions shall prevail

## Amendment 01
Tender No : SECI/C&P/MI/00/0011/2022-23
Design, Engineering, Supply, Construction, Erection, Testing, Commissioning including 5 Years Plant O&M of 2 MW (AC) Solar PV Power Plant with 01 MWh BESS at KAZA, Himachal Pradesh
S. No. | Section | Page No. | Clause | Original Version | Amendment
1 | SECTION - III Bid Data Sheet | 2 of 5 | 1 | The Contact Person is : BRIJ Mohan Sud Director (Technical). | The Contact Person is : Mr. Atul Bhatia, CEO, HRL Telephone No.: 7833880514
2 | Section VII - B | 89 of 136 | 16.2.3.3 | In case the contractor proposes to extend the column leg to embed it in the pile/pedestal as an alternate fixing arrangement, the column member shall be extended for full depth of the pile (100mm cover at tip of the pile) with an end plate of min. 4mm thickness to be welded at the bottom of column leg. (However, for plants in coastal area or in case of marshy soil the column post shall be supported only with base secured to foundation through base plate and anchor bolt assembly and no embedment of column leg in foundation is permitted) | In case the contractor proposes to extend the column leg to embed it in the pile/pedestal as an alternate fixing arrangement, the column member shall be extended for full depth of the pile (100mm cover at tip of the pile) with an end plate of min. 4mm thickness, projecting min. 50 mm beyond the face, to be welded at the bottom of column leg or an angle section of minimum 2mm thick to be bolted on either face of the column web at bottom end of the column (However, for plants in coastal area or in case of marshy soil the column post shall be supported only with base secured to foundation through base plate and anchor bolt assembly as per Cl. No. 13.26 and no embedment of column leg in foundation is permitted).
3 | Section VII - B | 100 of 136 | 35.1.9 | Module cleaning procedure and pressure requirement at discharge point shall be as per the recommendation of PV module manufacturer. However, discharge pressure at outlet shall not be less than 5 kgf/cm2(0.5 MPa) | Module cleaning procedure and pressure requirement at discharge point shall be as per the recommendation of PV module manufacturer. However, discharge pressure at outlet (connection point of flexible hose pipe) shall not be less than 5 kgf/cm2(0.5 MPa)
4 | Section VII - B | 89 of 136 | 16.2.3.3 | Security room/ cabin shall be a pre-engineered & pre-fabricated structure. The walls and roof of the building shall be fabricated with double skin insulated sandwiched AlZn alloy coated high tensile steel metal panels (BMT- 0.5mm, Al-Zn alloy coating -150 GSM total on both sides). The insulation shall be of PUF with min. density 40 kg/ cum and adequate thickness | Security room/ cabin shall be a pre-engineered & pre-fabricated structure. The walls and roof of the building shall be fabricated with double skin insulated sandwiched AlZn alloy coated high tensile steel metal panels (BMT- 0.5mm, Al-Zn alloy coating -150 GSM total on both sides). The insulation shall be of PUF with min. density 40 kg/ cum and 150 mm thickness.
5 | Section VII- B | 80 of 136 | 12.2.1 | However, the min. dia of the pile shall be 300mm (min. 350 mm for column web depth more than 175 mm) and 1800 mm respectively except when very hard strata/ rock (N>100) is encountered at a higher level, the pile shall be extended in to the hard strata minimum 1.5 times the diameter of the pile with total depth of the pile not less than 1200mm below cut-off level | However, the min. dia of the pile shall be 300mm (min. 350 mm for column web depth more than 175 mm) and 1500 mm respectively except when very hard strata/ rock (N>100) is encountered at a higher level, the pile shall be extended in to the hard strata minimum 1.5 times the diameter of the pile with total depth of the pile not less than 1200mm below cut-off level
6 | Section VII - B | - | 25.3 | New Clause | Heating Systems for MCR and Security Rooms: Oil flow type heat convectors each of 2000 Watts, 220 V AC of ISI mark shall be provided for MCR building(4 Nos.) and Security room(1 no.). These convectors shall have thermostatically controlled operation and shall be suitable for operating under specified climatic conditions. Power supply receptacles with DPMCB switches of adequate rating shall be provided in each room. These receptacles shall be fed from AC distribution board.
7 | Section VII - B SCC | 10 of 10 | 14 | New Clause related to early completion Incentive on Solar Part | The Contractor shall be paid an early completion commercial incentive of 1% of the Contract Price or INR 15 lakhs, whichever is lower, in case the Solar PV Part of the Project is commissioned by 30 Nov 2023 by the Contractor. The incentive will only be applicable against the commissioning of the entire Solar PV Capacity of 2 MW excluding BESS Part. Such incentive, if applicable, will be paid in toto along with the 70% payment milestone of the supply payments of the project.
8 | General | - | - | - | Clause related to Public Procurement Policy (PPP) applicability on this tender has been withdrawn and the withdrawl of this PPP Clause will supersede any other information/clause/format related to PPP appearing anywhrere in the tender document.