## Pre Bid Queries
“THE MANUFACTURING, TESTING, PACKING AND FORWARDING, SUPPLY AND TRANSPORTATION OF 400 MWP DOMESTICALLY MANUFACTURED SOLAR PV MODULES WITH DOMESTICALLY MANUFACTURED SOLAR CELLS”
Tender No : SECI/C&P/OP/11/011/2022-23
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Technical/Contractual) | Clarifications
1 | Section VII Scope of Supply and Technical Specifications (PART – A: SCOPE OF SUPPLY) | Page 3 of 18 | 1.4 | The Bidder shall offer only one type of PV Module with same Dimensions as per the specifications provided herein. The PV Module dimensions shall not change from the Guaranteed Technical Particular Datasheet (Form: T-01) provided with the bid. | Monocrystalline will be type either p(MonoPERC) or n (Topcon) cells modules. Are both acceptable to be considered in supplies? | Technical | Cell Technology shall be of one type only (i.e. either TopCon or MonoPERC). The Module dimensions shall not change from the GTP submitted with the bid.
2 | Section VII Scope of Supply and Technical Specifications (PART – A: SCOPE OF SUPPLY) | Page 3 of 18 | 1.5 | The Supplier shall submit PAN file of the PV Modules to be supplied (certified by an ILAC member signatory accredited laboratory) within 60 days from the date of Award. | Will it be acceptable if one or two bins PAN files are from laboratory and based on those one or two bins laboratory PAN files, other bins PAN files are internally submitted by manufacturer? | Technical | No PAN files of all the bins shall be certified by accredited laboratory as per the Clause.
3 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 5 of 18 | 2.1 | IS/IEC 61701: 2011: Salt Mist Corrosion Testing of Photovoltaic (PV) Modules – Severity 1 | Kindly confirm if manufacturer has- Severity - 6 test certificate as per IEC 61701: 2020. will it be acceptable? | Technical | Yes, it is acceptable
4 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 5 of 18 | 2.1 | IS 17210 (Part 1) : 2019: Photovoltaic (PV) Modules - Test Methods for the Detection of Potential-Induced Degradation, Part 1: Crystalline Silicon (under conditions of 85°C/85% RH for minimum 192 hours) | PID test sequence has already been included in latest IEC 61215:2021 version. Kindly consider: If manufacturer has IEC 61215 test certificate as per 2021 standard edition, IS 17210 (Part 1) : 2019 requirement will be considered as complied. | Technical | The terms and conditions of the tender document shall prevail.
5 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 5 of 18 | 3 | Module Efficiency≥ 21% | Please consider Module Efficiency≥ 20.9. Popular PV modules dimensions are 2278mm x 1133mm, so for minimum Wp 540Wp requirement, the efficiency would be 20.92%. | Technical | Kindly refer to Amendment 01
6 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 6 of 18 | 4.3 | The encapsulant shall have the following properties- Gel Content ≥ 75% for EVA; ≥ 70% for POE | Co-Extruded POE or EPE are popular Encapsulants, and can be used either in Glass/glass or glass/back sheet type of modules). Kindly consider to include Gel content as ≥ 70% for POE or EPE/Co-extruded POE. | Technical | Kindly refer to Amendment 01
7 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 7 of 18 | 4.7 | RFID tag which is embedded inside the module | Please consider to include two more options regarding RFID placement: 1- placing RFID outside laminate under the protective layer. 2- to have access of RFID from manufacturers website in case no physical RFID tag is placed in module.(We have been requesting MNRE for the 2nd option and in process of | Technical | Kindly refer to Amendment 01
8 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 8 of 18 | 5.2 | The modules shall be warranted for minimum of 10 years against all material/ manufacturing defects and workmanship. | Please consider : The modules shall be warranted for minimum of 10 years against all the defect which is impacting the performance of the modules. Excluding the defects which does not effecting the performance of modules. | Technical | The terms and conditions of the tender document shall prevail.
9 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 8 of 18 | 5.3 | The Supplier under this Contract (i.e. the Insurer) shall purchase an Insurance Policy (i.e. Buyer's cover) to insure it's contractual liabilities arising out of the long-term performance and product warranties as per Clause above on PV Modules to be supplied to the buyer (i.e. Beneficiary - SECI) under the Contract. The aggregate limit of Insurer's liability under this Policy in respect of all Photovoltaic Modules attaching to this Policy during the Policy Period shall be 100% of the Total Sum Insured, where Total Sum Insured shall be the total Invoice Value of capacity awarded under this Contract. This insurance should be valid for a period of 25 years from the date of energization or 6 months (180 days) beyond last delivery at site, whichever is earlier and the claim period should extend for a minimum of 1 year beyond this period (i.e. 25 years). | Supplier will have a single warranty insurance policy of certain capacity out of their total modules production capacity. Aggregate limit is generally considered around 5% (typically 3% to 7%) in all popular policies in market (e.g. Munich RE/Ariel RE). Insurer in Policy will be HDFC/Iffco Tokio kind of agencies while reinsurer would be Munich RE or Ariel RE. Warranty insurance certificates are issued by Insurer mentioning Total Sum Insured volume, project location, Customer name(e.g. SECI) and Sales contract reference details on completion of supplies to SECI. As per the popular policy terms, the warranty start date is considered with last date of modules supplies under the given sales contract. Period of performance warranty insurance will be 25 years from the warranty start date. Kindly consider to update the terms accordingly in this section of the tender. | Technical | An insurance policy purchased by the Supplier for their batch production capacity shall be acceptable. However, the Warranty Insurance certificate shall clearly identify the Beneficiary (i.e. SECI) along with project details viz. Location, Total Sum Insured and relevant contract reference details. Kindly refer to Amendment 01
10 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 8 of 18 | 6.3 | The BOM proposed shall be the subset of Constructional Data Form (CDF)s of all the test reports. | Please consider : The BOM proposed shall be the subset of IEC 61215/61730 Constructional Data Form (CDF)s and materials specifications in BOM will be as per IEC 61215/61730 and within limit of IEC 62915 latest retest guidelines. | Technical | BOM proposed shall be a subset of the IEC 61215/61730 CDFs along with extensions for alternate materials as per IEC 62915 Retesting guidelines, subject to suitability of the relevant BOM for other Type tests i.e. PID, Ammonia and Salt Mist. For e.g., PID test report with an alternate make of cell, not part of the BOM for IEC 61215, IEC 61730 shall not be acceptable.
11 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 9 of 18 | 7.2 | The Owner shall perform material inspection at the Manufacturer’s factory before the start of proposed manufacturing schedule. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification. | Please consider: The Owner shall perform material inspection at the Manufacturer’s factory either during modules manufacturing or during pre-dispatch Inspection. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification. | Technical | Kindly refer to Amendment 01
12 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 9 of 18 | 7.3 | The Manufacturing shall start only after the clearance by the Owner after the material inspection. | Kindly consider to remove this clause. | Technical | Kindly refer to Amendment 01
13 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 9 of 18 | 7.4 | The cells used for module making shall be free from all defects like edge chipping, breakages, printing defects, discoloration of top surface etc. Only Class A solar cell shall be used. | Please consider: The cells used for module making shall be qualified as per manufacturer's quality acceptance criteria of Class A solar cell. | Technical | The terms and conditions of the tender document shall prevail.
14 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 9 of 18 | 7.5 | The modules shall be uniformly laminated without any lamination defects. | Please consider: The modules shall be uniformly laminated without any lamination defects. Lamination Defects will be determined as per manufacturers acceptance criteria. | Technical | Inspection Criteria for Lamination defects is part of Visual Inspection, the inspection criteria for which shall be finalized after award of the contract prior to start of manufacturing. Pease refer Clause 8.2.
15 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 9 of 18 | 7.6 | Current binning of modules shall be employed so that current mismatch of modules in a pallet does not exceed 1% of Current at Maximum Power (Imp). | We have limitations in the sorter machines so only two bins possible with 150mA sorting range. So kindly consider, Current binning of modules to be employed at 150mA for one current bin & other current bin can be open. | Technical | The terms and conditions of the tender document shall prevail.
16 | Section VII Scope of Supply and Technical Specifications (Part C: PRE-DISPATCH INSPECTION PROTOCOL) | Page 11 of 18 | 6-Sampling Process | Flash Test, Visual Inspection, Electroluminescence | Please consider- Inspection Level : Special inspection level S4. | Technical | The terms and conditions of the tender document shall prevail.
17 | Section V Special Purchase Conditions (SPC) | Page 3 of 9 | 6 | The value of the Contract Performance Security shall be 5% (Five) of the Contract Value | We request to consider contract performance security to be 3% (three) of the contract value | Contractual | The terms and conditions of the tender document shall prevail.
18 | Section V Special Purchase Conditions (SPC) | Page 8 of 9 | 13 | Payment shall be released within 30 days of submission and acceptance of invoice by the Engineer In Charge, having following payment milestones as mentioned below. | We request as below: Payment shall be released within 15 days of submission and acceptance of invoice by the Engineer In Charge, having following payment milestones as mentioned below. | Contractual | The terms and conditions of the tender document shall prevail.
19 | Section V Special Purchase Conditions (SPC) | Page 4 of 9 | 6 | *Defective Modules : Modules found defective/damaged during the random physical/visual inspection or not having all weather worthy packing or improper palletizing or defects arising due to improper unloading. | We propose to remove the "defects arising due to improper unloading" as unloading is not in the scope of supplier. *Defective Modules : Modules found defective/damaged during the random physical/visual inspection or not having all weather worthy packing or improper palletizing or defects arising due to improper unloading. | Contractual | Kindly refer to Amendment 01
20 | SECTION - III BID DATA SHEETS (BDS) | Page 3 of 4 | 6 | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno-Commercial Bid (Envelope-I). | We request to keep the bid validity of 60 days | Contractual | The terms and conditions of the tender document shall prevail.
21 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | Page 5 of 18 | 1.2 | The PV Module shall be enlisted in ALMM – List I in accordance with extant provisions of Approved Models and Manufacturers of Solar Photovoltaic Modules (Requirements for Compulsory Registration, Order, 2019) and subsequent amendments. | Need clarity on the applicability of ALMM. We understand that ALMM would be required prior to the dispatch of the modules. Request you to please clarify | Contractual | All statutory and Government approval issued from time to time will prevail for the tender document and the bidders has to abide by that. Ex.: ALMM, Public Procurement, DCR regulation issued by MNRE etc.
22 | ANNEXURE TO BID DATA SHEET (BDS) QUALIFYING REQUIREMENTS | ANNEXURE TO BDS Page 4 of 9 | 1.2 | In the above case, the bidder shall submit following documentary evidence as credentials for the same: (iii) Sanction letter from the Distribution utility for Power Connection for the facility. | We request you to please consider the Agreement with the distribution utility for power connection also for this requirement | Contractual | The terms and conditions of the tender document shall prevail.
23 | ANNEXURE TO BID DATA SHEET (BDS) QUALIFYING REQUIREMENTS | ANNEXURE TO BDS Page 4 of 9 | 1.2 | In the above case, the bidder shall submit following documentary evidence as credentials for the same: (v) Annual Capacity Production certification. | We request you to please clarify the list of documents required for the Annual Capacity Production Certification. We would request that Certificate from Chartered Engineer should also be considered for this requirement. | Contractual | The terms and conditions of the tender document shall prevail.
24 | INVITATION FOR BIDS (IFB)/BID INFORMATION SHEET | 13 of 16(16/217) | L | OFFLINE & ONLINE BID-SUBMISSION DEADLINE - 23.12.2023 up to 1400 HRS | EMMVEE Requests to Extend the Bid Submission dates by 3-WEEKS AND provide new date with 13.01.2024 | Contractual | Any notification regarding extension of bid submission deadline (if any) will be notified on SECI's website and ETS Portal. However, SECI will ensure sufficient time for participation post the release of Amendment 1 & Clarifications.
25 | SPECIAL PURCHASE CONDITIONS (SPC) | 7 of 9 (134/217) | 13 | Schedule of Rates & Payments Terms of 10%, 80% & 10% | SECI to Confirm the LC will be for 100 % of the Contract Value/ Emmvee Request for 10% advance and balance 90% payment through Letter of Credit for 30 days prior to commencement of production. EMMVEE request you to establish an irrevocable Letter of Credit (L/C) in favour of the supplier through the Employer's Bank for payments. | Contractual | The terms and conditions of the tender document shall prevail.
26 | BID DATA SHEETS (BDS) | 72 | 6 | Bid Validity-The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno Commercial Bid (Envelope-I). | EMMVEE request to keep BID VALIDITY period to 30-days from date of opening of Techno-commercial bid. | Contractual | The terms and conditions of the tender document shall prevail.
27 | Bid Information Sheet | 13 of 16(16/217) | 16 | CONTRACT PERFORMANCE SECURITY - 5% of the Total Project/Order Cost for a total period of 27 months | Tender document Terms - 5% of Total PO VALUE EMMVEE Request to reduce it to 1% instead of 5%. | Contractual | The terms and conditions of the tender document shall prevail.
28 | SPC | 3 of 9 (129/217) | 25.6 | Contract Performance Security-25.1 The value of the Contract Performance Security shall be 5% (Five) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 27 Months (12 Months Project completion period) + 12 months of Defect Liability Period + 03 Months additional) from the date of its issuance. | Tender document Terms - 5% of Total PO VALUE EMMVEE Request to reduce it to 1% of PO Value instead of 5%. | Contractual | The terms and conditions of the tender document shall prevail.
29 | Defect Liability Period (GPC clause 53.2) | 133 | 3.2.13 | Add following to the existing clause: 53.2.13 Latent Defect Liability: Notwithstanding, the defect liability period of 12 months above, the contract shall carry a latent defect liability of 5 years from date of delivery of material at site towards any defects in the modules supplied by the Supplier. | Please delete Latent Defect Liability clause, as latent Defect liability is NOT applicable as per prevailing industry norms. | Contractual | The terms and conditions of the tender document shall prevail.
30 | BID DATA SHEETS (BDS) | 3 of 4 (72/217) | 7 | ZERO DEVIATION & REJECTION CRITERIA-Clause No. 18.1, Zero deviation & Clause No. 18.2, Rejection Criteria should be read in conjunction to each other & both clauses points mentioned should complement each other. | Unavoidable Deviations should be Allowed. | Contractual | The terms and conditions of the tender document shall prevail.
31 | SoS & TS - | 3 of 18 - 197 | PART – A: SCOPE OF SUPPLY -1 Scope of Supply | 1.1 The scope of supply includes Manufacturing, Testing, Packing and Forwarding, Transportation to Site and Unloading of domestically manufactured Solar PV Modules with domestically manufactured solar cells. | Please note unloading at site cannot be in the bidders scope as is currently mentioned in the clause, Please delete ''Unloading from bidders Scope'' also the words ''Unloading at site'' need to be deleted from the bidders scope as this is against industry practices. Unloading is Customer scope, Not in EMMVEE Scope | Contractual | Kindly refer to Amendment 01
32 | IFB | 15 of 16(18/217) | 6.0 Owner will place a single order for Purchase & Service: | (i) Purchase & Service Order: For providing the Ex Works-Supply, materials including mandatory spares and any other supplies specified in the Tender Documents under the scope of Supply. And for all services i.e., including Transportation and Insurance of all supplies till site, Unloading, and Handling at Site in respect of all the supplies and any other services specified in the Contract | Please delete ''Unloading & Handling at site from bidders Scope'' also the words ''Unloading and Handling at site in respect of all the supplies'' need to be deleted from the bidders scope as this is against industry practices. | Contractual | Kindly refer to Amendment 01
33 | GPC | 26 of 44 (108/217) | [E] PERFORMANCE OF SUPPLY - 40. Execution of Supply | 40.3 The Supplier shall arrange for loading, transportation & unloading of materials at project site at his own cost & risk. | Please delete ''Unloading from bidders Scope'' also the words ''Unloading of materials at project site at his own cost & risk'' need to be deleted from the bidders scope as this is against industry practices. | Contractual | Kindly refer to Amendment 01
34 | SoS & TS | 5 of 18 - 199 | PART – B: TECHNICAL SPECIFICATIONS - 2 Standards | IS 14286 (Part 1)-2019 - Terrestrial Photovoltaic (PV) Modules - Design Qualification and Type Approval, Part 1: Test Requirements (Second Revision) | IS 14286 (Part 1) – 2019-is equivalent IEC 61215(Part 1)-2016. Our modules are qualified for IEC61215;2021. No CRS Scheme available in BIS Portal for IS 14286 (Part 1) – 2019 | Technical | Please refer Clause 2.1. Higher revision of standards specified are acceptable
35 | SoS & TS | 5 of 18 - 199 | PART – B: TECHNICAL SPECIFICATIONS - 2 Standards | IS 14286: Part 1: Sec 1: 2019 - Terrestrial Photovoltaic (PV) Modules - Design Qualification and Type Approval, Part 1: Test Requirements, Section 1: Special requirements for testing of crystalline silicon photovoltaic (PV) modules (Second Revision) | IS 14286 (Part 1/Sec1) – 2019-is equivalent IEC 61215(Part 1/Sec 1)-2016. Our modules are qualified for IEC61215-2021. No CRS Scheme available in BIS Portal for IS 14286: Part 1: Sec 1: 2019 | Technical | Please refer Clause 2.1. Higher revision of standards specified are acceptable
36 | SoS & TS | 5 of 18 - 199 | PART – B: TECHNICAL SPECIFICATIONS -2 Standards | IS 16664: 2018 - Photovoltaic (PV) Modules- Ammonia Corrosion Testing | IS 16664 : 2018 - is equivalent IEC 62716:2013 . Request you to amendment for the same | Technical | IS 16664 : 2018 - is equivalent IEC 62716:2013. Please refer Clause 2.1. Equivalent IEC standard is acceptable
37 | SoS & TS | 5 of 18 - 199 | PART – B: TECHNICAL SPECIFICATIONS - 2 Standards | IS 17210: Part 1: 2019 - Photovoltaic (PV) Modules - Test Methods for the Detection of Potential-Induced Degradation, Part 1: Crystalline Silicon (under conditions of 85°C/85% RH for minimum 192 hours) | IS 17210: Part 1: 2019 is equivalent to IEC TS 62804-1. Request you to amendment for the same | Technical | IS 17210: Part 1: 2019 is equivalent to IEC TS 62804-1. Please refer Clause 2.1. Equivalent IEC standard is acceptable
38 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | 5 of 18 - 199 | 3. Technical Requirements | Module Efficiency - ≥ 21% & Power Rating at STC - ≥ 540 Wp | Module Efficiency of 540Wp - @ STC - ≥ 20.9%. & Please allow the N type Topcon solar module based on latest technology) . In Topcon technology efficiency is also higher than P Type PERC technology | Technical | TopCon technology is acceptable, subject to the minimum efficiency and Wattage criteria specified. The Supplier shall propose only one type of Cell technology with same dimensions (as provided with the bid).
39 | SOS &TS | 6 of 18 - 200 | PART B: TECHNICAL SPECIFICATIOS - 4 Component Specifications | 4.2 Back Sheet - The Owner reserves the right to conduct Pressure Cooker (PC) test/ Highly Accelerated Stress Test (HAST) to confirm the durability of the back sheet in accelerated conditions | Pressure Cooker (PC) test will be conduct at external lab @ with cost borne by Employers. Please confirm. | Technical | The cost of test conducted at external lab shall be borne by the Employer.
40 | SOS &TS | 6 of 18 - 200 | 4 Component Specifications | 4.2 encapsulant - ≥ 70% for POE (applicable for glass/glass modules) | Gel content - ≥ 60% for EVA+ POE (applicable for glass/glass module) & Gel content - ≥ 70% meets in Topcon technology withEPE/EPE combination - Request you to amendment for the same | Technical | Kindly refer to Amendment 01
41 | SOS &TS | 7/8 of 18 - 200/201 | 5 Warranty - 5.1 Performance Warranty | PV Modules shall be warranted for power output as mentioned by the bidder in the Degradation Curve for a minimum period of 25 years commencing from energization of system or 6 months (180 days) beyond last delivery at site, whichever is earlier. | Please clarify the same shall be applicable from the date of Tax Invoice | Technical | The terms and conditions of the tender document shall prevail.
42 | SOS &TS | 7/8 of 18 - 202 | 5 Warranty - 5.3 Warranty Insurance | The aggregate limit of Insurer's liability under this Policy in respect of all Photovoltaic Modules attaching to this Policy during the Policy Period shall be 100% of the Total Sum Insured, where Total Sum Insured shall be the total Invoice Value of capacity awarded under this Contract. This insurance should be valid for a period of 25 years from the date of energization or 6 months (180 days) beyond last delivery at site, whichever is earlier and the claim period should extend for a minimum of 1 year beyond this | Please clarify the same shall be applicable as ---The aggregate limit of Insurer's liability under this Policy in respect of all Photovoltaic Modules attaching to this Policy during the Policy Period shall be 6% of the Total Sum Insured, where Total Sum Insured shall be the total Invoice Value of capacity awarded under this Contract. This insurance should be valid for a period of 25 years from the date of Tax Invoice or 6 months, within the date of Tax Invoice whichever is earlier. | Contractual | Kindly refer to Amendment 01
43 | SOS &TS | 10 of 18 - 204 | PART – C: PRE-DISPATCH INSPECTION PROTOCOL - 4.0 Inspection Schedule | The Supplier shall propose the schedule for Pre-dispatch Inspection of finished goods to the Owner well in advance, and in no case less than 07 (Seven) days prior to commencement of inspection. Production Flash Test Results of the offered PV Modules shall be submitted to the Owner along with the inspection call. | Please replace 7 days PDI by 2-3 days in this clause in line with industry practice. Pre Dispatch Inspection will be 5MW/lot | Technical | The terms and conditions of the tender document shall prevail.
44 | SOS &TS | 11 of 18 - 204 | 5.1 BOM verification | The details of materials used will be verified from the ERP/Manufacturing data and corroborated with the approved Bill of Materials. | Please change this BOM material shall be verified in the shop-floor. | Technical | The BoM shall be verified at shop floor. The Supplier may corroborate the validity of the same through documentation from manufacturing data.
45 | SOS &TS | 11 of 18 - 205 | 6.0- Sampling Process | Flash Test - General inspection level I | Special Inspection Level S-4 | Technical | The terms and conditions of the tender document shall prevail.
46 | SOS &TS | 11 of 18 - 205 | 6.0- Sampling Process | Visual Inspection -General inspection level I | Special Inspection Level S-4 | Technical | The terms and conditions of the tender document shall prevail.
47 | SOS &TS | 11 of 18 - 205 | 6.0- Sampling Process | Electroluminescence-General inspection level I | Special Inspection Level S-4 | Technical | The terms and conditions of the tender document shall prevail.
48 | SOS &TS | 11 of 18 | 6.0- 1 & 2 Sampling Process | The inspector(s) shall commence inspection process by randomly selecting samples from the list of module serial numbers (pallet-wise) provided by Supplier. | The clause needs to change and incorporate that sample shall be selected from box number list instead of Module serial numbers in line with industry practice. | Technical | The Clause mentions (pallet-wise), thereby already addressing the query.
49 | BID DATA SHEETS (BDS) | 72 | 7 | ZERO DEVIATION & REJECTION CRITERIA | Clause No. 18.1, Zero deviation & Clause No. 18.2, Rejection Criteria should be read in conjunction to each other & both clauses points mentioned should complement each other. | Contractual | The terms and conditions of the tender document shall prevail.
50 | DOMESTIC CONTENT REQUIREMENT | 9 | 3 | For the supplies to be done under this tender, both the Solar Cells and Modules must be made in India and Modules shall be from the Manufacturers listed in ALMM list, published & updated by MNRE from time to time | ALMM at the time of last supply | Contractual | All statutory and Government approval issued from time to time will prevail for the tender document and the bidders has to abide by that. Ex.: ALMM, Public Procurement, DCR regulation issued by MNRE etc.
51 | Technical Eligibility Conditions | 76 | 1.2 | a. The bid can only be submitted by an original PV Module Manufacturer, meeting any of the below criteria:  The PV Module manufacturer having a manufacturing facility capacity of minimum 133 MWp/ annum if: Submitting its bid for Package Capacity of 100 MWp Route-I: The bidders manufacturing facility of PV module is existing and under production: Route-II: The bidders manufacturing facility of PV module is under pipeline/construction: | Possibility of manufacturing at ALMM certified alternate facility. | Contractual | All statutory and Government approval issued from time to time will prevail for the tender document and the bidders has to abide by that. Ex.: ALMM, Public Procurement, DCR regulation issued by MNRE etc.
52 | Rights of the Owner to forfeit Contract Performance Security | 97 | 22 | Whenever any claim against the Supplier for the payment of a sum of money arises out of or under the Contract, the Supplier shall pay to the Owner on demand any balance remaining due to the Owner & Owner shall be entitled to recover such sum by appropriating in part or whole from the Contract Performance Security of the Supplier. In the event of the security being insufficient or if no security has been taken from the Supplier, then the balance or the total sum recoverable, as the case may be shall be deducted from any sum then due or which at any time thereafter may become due to the Supplier. | QUERY | Contractual | Query not clear.
53 | Component Specifications | 201 | 4.6 | The cable length shall be finalized after award of the contract. | Specify Cable length of JB | Technical | Kindly refer to Amendment 01
54 | Warranty | 202 | 5.3 | The Supplier under this Contract (i.e. the Insurer) shall purchase an Insurance Policy (i.e. Buyer's cover) to insure it's contractual liabilities arising out of the long-term performance and product warranties as per Clause above on PV Modules to be supplied to the buyer (i.e. Beneficiary - SECI) under the Contract. The aggregate limit of Insurer's liability under this Policy in respect of all Photovoltaic Modules attaching to this Policy during the Policy Period shall be 100% of the Total Sum Insured, where Total Sum Insured shall be the total Invoice Value of capacity awarded under this Contract. This insurance should be valid for a period of 25 years from the date of energization or 6 months (180 days) beyond last delivery at site, whichever is earlier and the claim period should extend for a minimum of 1 year beyond this period (i.e. 25 years). | Price to be quoted including or excluding TPI. | Technical | Price quoted shall ne inclusive of the TPI. Please refer Amendment to the Clause.
55 | Sampling Process | 204 | 6 | The inspector(s) shall commence inspection process by randomly selecting samples from the list of module serial numbers (pallet-wise) provided by Supplier. Number of samples shall be chosen as per the inspection level mentioned in the table below and ISO 2859-1 (Single Sampling Plan for Normal Inspection). | Mention the lot size for PDI & no of maximum visits possible by the inspector. | Technical | The lot size for PDI shall be finalised with the Supplier after the Award of the Contract.
56 | SoS and TS | 5 | 3 | Module Efficiency ≥ 21% | TPSSL request SECI to kindly reduce the Module Efficiency to ≥ 20.4% | Technical | Kindly refer to Amendment 01
57 | ANNEXURE TO BID DATA SHEET (BDS) QUALIFYING REQUIREMENTS | - | - | Technical and Financial eligibility conditions | TPSSL requests SECI to confirm that, we can Participate in the tender as TP Solar Ltd (New Manufacturing Plant) using Technical/Financial credentials of Tata Power Solar Systems Limited (Old Manufacturing Plant) to fulfil the QUALIFYING REQUIREMENTS (QR) Both TP Solar Limited & Tata Power Solar Systems Limited are 100% Subsidiary of Tata Power Renewable Energy Limited. | Contractual | Your understanding is correcr. It is allowed.
58 | Delivery Schedule | 2 | 3 | Delivery Schedule: The Time for Completion for the entire 400 MWp (DC) Solar PV Module Package in total shall be 12 (Twelve) Months from the Date of the Contract Agreement / Purchase & Service Order. | TPSSL request SECI to kindly confirm That total allotted capacity can be Supplied in last 10 to 20 Days (i.e. within 340th to 360th Days) | Contractual | No. The detailed delivery schedule will be shared with the successful supplier after the signing of Contract Agreement and the supplier has to diligently abide by that. However the total supply window will be of 09 months as mentioned in SPC section of the tender document.
59 | SoS and TS | 5 | 3 | Power Rating at STC ≥540Wp | We request SECI to Kindly Make the Power rating as ≥520 @ efficiency > 20% | Technical | Kindly refer to Amendment 01
60 | SoS and TS | - | 4.3 | Gel Content ≥ 75% for EVA; ≥ 70% for POE (applicable for glass/glass modules) | We request to include ≥ 70% for EPE (applicable for glass/glass modules) | Technical | Kindly refer to Amendment 01
61 | Standards | 199 | 2.1 | IS 16664: 2018 Photovoltaic (PV) Modules- Ammonia Corrosion Testing IS 17210: Part 1: 2019 - Photovoltaic (PV) Modules - Test Methods for the Detection of Potential-Induced Degradation, Part 1: Crystalline Silicon (under conditions of 85°C/85% RH for minimum 192 hours) | Kindly accept the below request Ammonia Test Certificate will be as per IEC 62716 PID Test Report will be as per IEC 62804 | Technical | Please refer Clause 2.1. Higher revision of standards specified are acceptable
62 | Technical Requirements | 199 | 3 | Power Rating at STC ≥ 540 Wp | As the DCE cell efficiency are under ramp up and considering efficiency curve we would like to propose Power Rating at STC ≥ 525 Wp. So that we can bid higher capacity. | Technical | The terms and conditions of the tender document shall prevail.
63 | SECTION – VII SCOPE OF SUPPLY & TECHNICAL SPECIFICATIONS | 202 | 5.3 Warranty Insurance | 5.3 Warranty Insurance The Supplier under this Contract (i.e. the Insurer) shall purchase an Insurance Policy (i.e. Buyer's cover) to insure it's contractual liabilities arising out of the long-term performance and product warranties as per Clause above on PV Modules to be supplied to the buyer (i.e. Beneficiary - SECI) under the Contract. The aggregate limit of Insurer's liability under this Policy in respect of all Photovoltaic Modules attaching to this Policy during the Policy Period shall be 100% of the Total Sum Insured, where Total Sum Insured shall be the total Invoice Value of capacity awarded under this Contract. This insurance should be valid for a period of 25 years from the date of energization or 6 months (180 days) beyond last delivery at site, whichever is earlier and the claim period should extend for a minimum of 1 year beyond this period (i.e. 25 years). | Kindly accept the below clause for module warranty insurance as per other CPSUs. Module performance Insurance: To ensure faithful performance of PV modules, Bidder must submit an insurance with a coverage of minimum 6 % of total order value of the supplies envisaged under the contract for 25 years, with the employer as its beneficiary. Any financial implication encountered due to insurance shall be borne by the bidder. The Bidder’s insurance liabilities pertaining to the scope of works are detailed out in elsewhere in Bidding Document. The module should be insured as per the following clauses are to be complied: i. It has to be issued from one of the companies as listed below: a) Swiss RE b) Munich RE c) Power Guard d) Ariel RE | Technical | Kindly refer to Amendment 01
64 | Technical Requirements | 199 | 3 | Module Efficiency ≥ 21% | Kindly accept Mod Eff. >=20.30% (as per cell eff curve) | Technical | Kindly refer to Amendment 01
65 | Component Specifications | 200 | 4.3 Component Specifications | Gel content ≥ 75% for EVA; | Gel content ≥ 65% for EVA; | Technical | Kindly refer to Amendment 01
66 | Component Specifications | 200 | 4.3 Component Specifications | Use of EVA & POE (in dual glass) | We would like to propose below configuration 1. Glass to transparent back sheet- Front EVA and back EPE 2.Dual Glass - Front and back EPE in stead of POE as per tender condition | Technical | EPE instead of POE for glass/glass modules is acceptable. Please refer Amendment
67 | Component Specifications | 200 | 4.2 | The Owner reserves the right to conduct Pressure Cooker (PC) test/ Highly Accelerated Stress Test (HAST) to confirm the durability of the back sheet in accelerated conditions. | PCT facility is not available in-house | Technical | The Owner shall bear the cost of PCT at testing laboratory, if required.
68 | Manufacturing & Inspection | 203 | 7.5 | The modules shall be uniformly laminated without any lamination defects | Acceptance of modules will be as per Premier's acceptance criteria | Technical | Details of Inspection Criteria shall be finalised with the Supplier after Award of Contract. Please refer Clause 8 of PART – C: PRE-DISPATCH INSPECTION PROTOCOL
69 | Manufacturing & Inspection | 203 | 7.6 | Current binning of modules shall be employed so that current mismatch of modules in a pallet does not exceed 1% of Current at Maximum Power (Imp). Different colour codes shall be provided on the modules as well as pallet for identification of different bins. Maximum three nos. of bins will be allowed. | Upto #3 current binned (Imp) modules will be provided / each current bin (Imp) will be of 0.250A (250mA) | Technical | The terms and conditions of the tender document shall prevail.
70 | Pre Dispatch Inspection Protocol | 205 | 6 (i) | 1. Flash Test General inspection level I 2. Visual Inspection General inspection level I 3. Electroluminescence General inspection level I 4. Electrical Characteristics Special inspection level S-2 | As per ISO 2859-1, following inspection level will be following during PDI/PSI: 1. Flash Test : Special inspection level / S4 (AQL 2.5) 2. Visual Inspection : Special inspection level / S4 (AQL 2.5-Major, 4.0-Minor) 3. Electroluminescence : Special inspection level / S4 (AQL 2.5-Major, 4.0-Minor) 4. Electrical Characteristics (DCW/IR/GD) : Special inspection level S-4 (AQL 2.5) 5. Wet Leakage Test : #2 modules/lot (AQL 2.5) | Technical | The terms and conditions of the tender document shall prevail.
71 | BDS | Page 3 of 4 | Sl No. 6 (BID VALIDITY) | The bid validity period shall be 180 (One Hundred and Eighty Days) from the date of opening of Techno-Commercial Bid (Envelope-I). | Wafer is the key component of this project and the Market price of wafer is highly volatile, request you to kindly consider for 60/90 days. | Contractual | The terms and conditions of the tender document shall prevail.
72 | SPC | Page 8 of 9 | Clause No. 13 (Schedule of Rates & Payments) | Payment shall be released within 30 days of submission and acceptance of invoice by the Engineer In Charge, having following payment milestones as mentioned below. A. The payment against Supply portion shall be made as per the following terms and conditions: i) Interest free advance of 10% of the total value of Supply portion shall be released to supplier against Submission of Test Certificates / Manufacturing Clearance, detailed Performa invoice of contractor and against submission of unconditional & irrevocable Advance Bank Guarantee (ABG) with a validity period up to date of final supply amounting to 100% of total advance amount. The ABG needs to be submitted in addition to the Contract Performance Security. | 1. 1stly, as every manufactures are facing huge Working capital shortage. 2ndly as this is going to be fixed price contract we need to procure the entire wafer upon award of contract. Hence we request you to kindly increase the advance to 20%. Also, we request you to accept POI (Payment Order Instrument) against this advance amount. We believe, this payment term will lead to discovery of better prices in the bid. 2. In addition, we request that you kindly amend the payment clause. The remaining 80% payment is made via LC (Letter of Credit). | Contractual | The terms and conditions of the tender document shall prevail.
73 | SPC | Page 3 of 9 | 6. Contract Performance Security (GPC clause 25) | 25.1 The value of the Contract Performance Security shall be 5% (Five) of the Contract Value (i.e., total sum of the Supply & Service Contract). This Performance security will be valid for a total period of 27 Months (12 Months Project completion period) + 12 months of Defect Liability Period + 03 Months additional) from the date of its issuance. 25.4 Bank Guarantee towards Contract Performance Security shall be from any scheduled bank as specified in the List of Banks enclosed at Form F-17, Section - VI, Sample Forms and Formats of Tender documents or a branch of an International Bank situated in India and registered with Reserve Bank of India as scheduled foreign bank in case of Indian bidder. | We request you to kindly consider CPG for 3% and accept an Insurance Surety Bond from an Insurer as per guidelines issued by Insurance Regulatory and Development Authority of India (IRDAI). 3% CPG is also widely accepted by PSUs like NTPC and NLC's recent tenders. | Contractual | The terms and conditions of the tender document shall prevail.
74 | ITB | Page 13 of 50 | 15 EARNEST MONEY DEPOSIT (EMD) | EARNEST MONEY DEPOSIT (EMD) : 15.2 The Bids must be accompanied with 'Earnest Money Deposit (EMD)' in the form of either through NEFT/ RTGS transfer in the account of SECI or 'Demand Draft' or 'Banker's Cheque' [in favour of Solar Energy Corporation of India limited, New Delhi payable at New Delhi] or 'Bank Guarantee' as per the format given in Form F - 3 of the bidding documents. Bidders shall ensure that EMD, having a validity of at least 30 (Thirty) Days beyond the validity of the bid, must accompany the Bid in the format(s) made available in the Tender Document. | We request that you kindly consider EMD in the form of a surety bond from an insurer as per guidelines issued by the Insurance Regulatory and Development Authority of India (IRDAI). | Contractual | The terms and conditions of the tender document shall prevail.
75 | SoS & TS | Page 3 of 18 | 1.1 | Unloading of modules at site is in the scope of bidders | As per prudent practise We request SECI to remove unloading of modules from the manufacturers scope and keep in the BOS/EPC contractor scope | Contractual | Kindly refer to Amendment 01
76 | SoS & TS, ITB | Page 3 of 18,Page 23 of 50 | 1.6. 31.4 | Delivery Location- Ramagiri, Anantapur, Andhra Pradesh…....The freight charges (including taxes) for 2000 kms will be considered for the purpose of evaluation, | The delivery location is already given and also in the other clause transportation of 2000 km is kept, seems there is contradiction, please clarify what needs to be considered | Contractual | Kindly refer to Amendment 01
77 | IFB | Page 13 of 16 | (I) | EMD | We request SECI to accept Bid security declaration in place of EMD as per the | Contractual | The terms and conditions of the tender document shall prevail.
78 | IFB | Page 13 of 16 |  | CPBG- 5% for 27 months | The completion period is 360 days, please accept CPBG for 12 months instead of 27 months | Contractual | The terms and conditions of the tender document shall prevail.
79 | ITB | Page 29 of 50 | V | Mechanism for L1 matching: | Please clarify, the in RA only L1 bidder will be awarded the Quoted Capacity, Other bidder from L2, L3… need to match the L1 Price if any balance capacity is left after L1 Awarded Capacity as the same is not clear in the tender clauses. | Contractual | Yes the understanding is correct.
80 | BDS | Page 3 of 4 | Sl 6 | Bid Validity - 180 days from opening of Envelope 1 (Techno-Commercial Bid) | We request SECI to make the bid validity as 90 days from Opening of Envelope 1 | Contractual | The terms and conditions of the tender document shall prevail.
81 | ANNEXURE TO BDS | Page 4 of 9 | 1.2 | A summarized sheet of average turnover, certified by a practicing Chartered Accountant/Statutory Auditor should be compulsorily enclosed along with corresponding annual accounts. | Bidder is already submitting balance sheet containing all the details and breakup, additional requirement of Certificate from practicing Chartered Accountant/Statutory Auditor is an unnecessary requirement. Pls remove this requirement. | Contractual | The terms and conditions of the tender document shall prevail.
82 | SPC | Page 7 of 9 | 53.2.13 | Latent defect- 5 years | Latent Defect should be in concurrence to DLP, 12 months from receipt at site, pls accept | Contractual | The terms and conditions of the tender document shall prevail.
83 | SPC | Page 9 of 9 | 78 | Payment terms | Please also have provision to make the payment through Letter of Credit | Contractual | The terms and conditions of the tender document shall prevail.
84 | General | - | - | Minimum and maximum Wp of module | Please clarify if there is any minimum or maximum Wp of modules required. | Technical | Please refer Clause 3 of Part B: Technical Specifications.
85 | General | - | - | Cell/ Module Technology | Monofacial or Bifacial Module Please Confirm | Technical | Monofacial Cells
86 | General | - | - | 1 Flash Test - General inspection level I | Please Accept Special Inspection Level S4 | Technical | The terms and conditions of the tender document shall prevail.
87 | General | - | - | 2 Visual Inspection - General inspection level I | Please Accept Special Inspection Level S4 | Technical | The terms and conditions of the tender document shall prevail.
88 | General | - | - | 3 Electroluminescence - General inspection level I | Please Accept Special Inspection Level S4 | Technical | The terms and conditions of the tender document shall prevail.
89 | General | - | - | 4 Electrical Characteristics - Special inspection level S-2 | Please Accept Special Inspection Level S4 | Technical | The terms and conditions of the tender document shall prevail.
90 | General | - | - | De-loading factor for higher module | Is there any Evaluation / deloading factor for higher Wp module Supply | Technical | There is no provision for evaluation/deloading factor for higher Wp Module Supply.
91 | General | - | - | Price variation | Please include Price variation | Contractual | The terms and conditions of the tender document shall prevail.

## Amendment 01
“THE MANUFACTURING, TESTING, PACKING AND FORWARDING, SUPPLY AND TRANSPORTATION OF 400 MWP DOMESTICALLY MANUFACTURED SOLAR PV MODULES WITH DOMESTICALLY MANUFACTURED SOLAR CELLS”
Tender No : SECI/C&P/OP/11/011/2022-23
Sl. No. | Tender Section | Page No. | Clause No | Original Version | Amendment
1 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | 7/8 of 18 - 202 | 5.3 | The aggregate limit of Insurer's liability under this Policy in respect of all Photovoltaic Modules attaching to this Policy during the Policy Period shall be 100% of the Total Sum Insured, where Total Sum Insured shall be the total Invoice Value of capacity awarded under this Contract. This insurance should be valid for a period of 25 years from the date of energization or 6 months (180 days) beyond last delivery at site, whichever is earlier and the claim period should extend for a minimum of 1 year beyond this | The aggregate limit of Insurer's liability under this Policy in respect of all Photovoltaic Modules attaching to this Policy during the Policy Period shall be 6% of the Total Sum Insured, where Total Sum Insured shall be the total Invoice Value of capacity awarded under this Contract. This insurance should be valid for a period of 25 years from the date of energization or 6 months (180 days) beyond last delivery at site, whichever is earlier and the claim period should extend for a minimum of 1 year beyond this. Warranty Insurance certificate shall clearly identify the Beneficiary (i.e. SECI) along with project details viz. Location, Total Sum Insured and relevant contract reference details.
2 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) |  | 4.7 | Each PV Module shall be provided with a RFID tag which is embedded inside the module lamination and must be able to withstand harsh environmental conditions. The RFID data base shall contain the following information. RFID scanner and database of all the modules containing the following information shall also be provided. (i) Name of the Manufacturer of PV Module (ii) Name of the Manufacturer of Solar cells (iii) Type of cell (iv) Month and year of the manufacture (separately for solar cells and module) (v) Country of origin (separately for solar cells and module) (vi) I-V curve for the module (vii) Peak Wattage, Im, Vm and FF for the module (viii) Unique Serial No. and Model No. of the module. (ix) Date and year of obtaining IEC PV module qualification certificate (x) Name of the test lab issuing IEC certificate (xi) Other relevant information on traceability of solar cells and modules as per ISO 9000 series. | The following information must be mentioned in the RFID used on each module (This can be inside or outside the laminate, but must be able to withstand harsh environmental conditions): i. Name of the manufacturer of PV Module ii. Name of the Manufacturer of Solar cells iii. Month and year of the manufacture (separately for solar cells and module) iv. Country of origin (separately for solar cells and module) v. I-V curve for the module at Standard Test Condition (1000 W/m 2 , AM 1.5, 250 C) vi. Wattage, Im, Vm and FF for the module vii. Unique Serial No. and Model No. of the module viii. Date and year of obtaining IEC PV module qualification certificate ix. Name of the test lab issuing IEC certificate x. Other relevant information on traceability of solar cells and module as per ISO 9000 Site owners would be required to maintain accessibility to the list of Module IDs along with the above parametric data for each module.
3 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | 5 of 18 - 199 | 3 | Module Efficiency - ≥ 21% & Power Rating at STC ≥ 540 Wp | Module Efficiency - ≥ 20.9% & Power Rating at STC ≥ 540 Wp
4 | SOS &TS | 6 of 18 - 200 | 4.3 | Parameter: Gel Content Value: ≥ 75% for EVA; ≥ 70% for POE (applicable for glass/glass modules) | Parameter: Gel Content Value: ≥ 75% for EVA (applicable for glass/polymer modules) ≥ 70% for POE or EPE i.e. EVA co-extruded with POE (applicable for glass/glass modules or glass/polymer modules)
5 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 8 of 18 | 6.3 | The BOM proposed shall be the subset of Constructional Data Form (CDF)s of all the test reports. | The BOM proposed shall be the subset of IEC 61215/61730 Constructional Data Form (CDF)s, subject to suitability of the proposed BOM for other type tests the relevant BOM Extensions for BOM components shall be in accordance with IEC 62915 retest guidelines.
6 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 9 of 18 | 7.2 | The Owner shall perform material inspection at the Manufacturer’s factory before the start of proposed manufacturing schedule. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification. | The Owner shall perform material inspection at the Manufacturer’s factory during manufacturing of Modules or during pre-dispatch Inspection. Proof of procurement of components as per the approved BOM mentioning manufacturer name, manufacturing date and relevant test certificate shall be submitted during material inspection for verification.
7 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | Page 9 of 18 | 7.3 | The Manufacturing shall start only after the clearance by the Owner after the material inspection. | Void
8 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) | 3 of 18 - 197 | 1.1 | The scope of supply includes Manufacturing, Testing, Packing and Forwarding, Transportation to Site and Unloading of domestically manufactured Solar PV Modules with domestically manufactured solar cells. | The scope of supply includes Manufacturing, Testing, Packing and Forwarding, Transportation to site of domestically manufactured Solar PV Modules with domestically manufactured solar cells. Unloading of the consignment (i.e. PV Modules supplied under this Contract) shall be the responsibility of the Employer. However, the Supplier shall depute an authorised representative to the site commencing from the date of delivery of first consignment till the completion of all Supplies under this Contract for verification of receipt of the consignment in good condition, and to facilitate the handing over of the same to the Employer/Employer's assignee. Any physical damages identified during the process shall be jointly documented in a measurement sheet. The Supplier shall replace the damaged/defective modules as per the terms of the Contract. As mentioned, the unloading part of the Modules will be under Employer's scope and this change related to the Unloading will supersede any other earlier clause related to the Unloading, anywhere mentioned in the tender document.
9 | Section VII Scope of Supply and Technical Specifications (PART – B: TECHNICAL SPECIFICATIONS) |  | 4.6 | The material used for junction box shall be UV resistant to avoid degradation during module life. The degree of protection of the junction box shall be at least IP 67. Minimum three number of bypass diodes (not applicable for thin-film Modules) and two number of IS 16781 / IEC 62852 certified MC4 compatible connectors with appropriate length of IS 17293 / IEC 62930 certified 2.5 sq.mm. or higher copper cable shall be provided. The cable length shall be finalized after award of the contract. | The material used for junction box shall be UV resistant to avoid degradation during module life. The degree of protection of the junction box shall be at least IP 67. Minimum three number of bypass diodes and two number of IS 16781 / IEC 62852 certified MC4 compatible connectors with IS 17293 / IEC 62930 certified 4 sq.mm. copper cable of 1200 mm length shall be provided.
10 | Section I Invitation for Bids (IFB) | 5 of 16 | 2.13
11 | Section I Invitation for Bids (IFB) | 15 of 16 | 6 | (i) Purchase & Service Order: For providing the Ex Works-Supply, materials including mandatory spares and any other supplies specified in the Tender Documents under the scope of Supply. And for all services i.e., including Transportation and Insurance of all supplies till site, Unloading, and Handling at Site in respect of all the supplies and any other services specified in the Contract. | (i) Purchase & Service Order: For providing the Ex Works-Supply, materials including mandatory spares and any other supplies specified in the Tender Documents under the scope of Supply. And for all services i.e., including Transportation and Insurance of all supplies till site in respect of all the supplies and any other services specified in the Contract.
12 | Section II Instructions to Bidders (ITB) | 44 of 50 | 10 (II) A | Following documents must be supplied in addition to online document as a part of first envelope. | (s) Form T-01 (Guarantee Technical Particular Datasheet) (t) Form T-02 (Degradation Curve of PV Module)
13 | Section V Special Purchase Conditions (SPC) | 2 of 9 | 3
14 | Section V Special Purchase Conditions (SPC) | 4 of 9 | 25.3 | *Defective Modules : Modules found defective/damaged during the random physical/visual inspection or not having all weather worthy packing or improper palletizing or defects arising due to improper unloading. | *Defective Modules : Modules found defective/damaged during the random physical/visual inspection or not having all weather worthy packing or improper palletizing.
15 | Section VII Scope of Supply and Technical Specifications (PART – A: Scope of Supply) | 3 of 18 | 1.3 | The Owner reserves the right to increase or decrease the quoted PV Module capacity by ± 10% at the time of placing of the order on the same price, terms and conditions of the contract. The Owner also reserves the right to order up to additional 5% of awarded PV Module capacity on the same price, terms and conditions of the contract, during the currency of the contract by giving suitable extension in delivery period for the additional quantity | The Owner reserves the right to increase or decrease the quoted PV Module capacity by ± 10% at the time of placing of the order on the same price, terms and conditions of the contract. The Owner also reserves the right to order up to additional 100% of awarded PV Module capacity on the same price, terms and conditions of the contract as detailed in the IFB Section of the tender document.
16 | Schedule of Rate | - | - | - | The updated Schedule of Rate is attached separately with Amendment 01 to the tender document, having updates in the SOR 2 sheet. This Newly uploaded/revised SOR Sheet will supersede the earlier version of SOR. The Financial bids quoted under earlier SOR sheet will be summarily rejected.
17 | Section II Instructions to Bidders (ITB) | 23 of 50 | 31.4 | Total 2000 kms have been considered as the tentative distance between the works of the bidder and Owner's site in Schedule No. 2. Bidders are required to quote the unit rate of freight on per km basis accordingly. The freight charges (including taxes) for 2000 kms will be considered for the purpose of evaluation, however, the freight payment will be done based on the shortest distance of the site from the works. | Bidders are required to quote the Distance of the "Supplier Works to Ramagiri Site (in Kms)" & accordingly needs to quote the Unit Freight Charges (INR/MWp/Km) in the updated SOR 2 sheet. Accordingly, the total Freight Charges will be ascertained for arriving to the total FOR Destination basis cost & accordingly will also be used for the Freight Payment on the distance basis. Further, this Unit Freight Charges (INR/MWp/Km) as mentioned under the SOR 2, will also be used for the purpose of deriving the L1 position of the bidder for Repeat Order (if any) (based on the actual distance of the Supplier's Work to the Repeat Order site) and accordingly, L1 bidder will be decided for placement of Repeat Order (If any) & accordingly will also be used for the Freight Payment on the distance basis.
18 | Section V Special Purchase Conditions (SPC) | 8 of 9 | 13 | Total 2000 kms have been considered as the tentative distance between the works of the bidder and Owner's site. Bidders are required to quote the unit rate on per km basis accordingly. This 2000 kms will be considered for the purpose of evaluation, however, the freight payment will be done based on the actual running km/distance of the site from the works. | Bidders are required to quote the Distance of the "Supplier Works to Ramagiri Site (in Kms)" & accordingly needs to quote the Unit Freight Charges (INR/MWp/Km) in the updated SOR 2 sheet. Accordingly, the total Freight Charges will be ascertained for arriving to the total FOR Destination basis cost & accordingly will also be used for the Freight Payment on the distance basis. Further, this Unit Freight Charges (INR/MWp/Km) as mentioned under the SOR 2, will also be used for the purpose of deriving the L1 position of the bidder for Repeat Order (if any) (based on the actual distance of the Supplier's Work to the Repeat Order site) and accordingly, L1 bidder will be decided for placement of Repeat Order (If any) & accordingly will also be used for the Freight Payment on the distance basis.