## Amendment - 1
NIT No: SECI/C&P/NIT/2018/SCCL100
Tender for Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 90 MW (AC) Solar PV Power Plant under different packages including 10 years plant O&M at Singareni Collieries Company Limited, Telangana, India
Sl. No. | Section | Page No. | Clause | Original Version | Amendment
1 | SECTION - VII SCOPE OF WORKS & TECHNICAL SPECIFICATIONS | Page 84 of 136 | 21.1.1 | The Contractor shall provide minimum 4 (four) number of secondary standard pyranometers (ISO 9060 classification) along with necessary accessories for measuring the incidental solar radiation at horizontal and inclined plane of array. | The Contractor shall provide minimum 2 (two) number of secondary standard pyranometers (ISO 9060 classification) along with necessary accessories under each package or site - one for measuring the incidental solar radiation at horizontal and the other for measuring incidental solar radiation in the inclined plane of array.
2 | SECTION - VII SCOPE OF WORKS & TECHNICAL SPECIFICATIONS | Page 115 of 136 | 38.25 | Modules shall be clamped & bolted with the structure properly. The material of clamps shall be Al / SS – 316 having weather resistant properties. Clamp/bolt shall use EPDM rubber and shall be designed in such a way so as not to cast any shadow on the active part of a module | The Module should be fastened to the module mounting structure with clamps or frame bolt holes. The material of clamps shall be Al / SS – 316 having weather resistant properties. Clamp/bolt shall use EPDM rubber and shall be designed in such a way so as not to cast any shadow on the active part of a module. The Module mounting methodology shall be as per the Installation Manual of the PV Module manufacturer to withstand the mechanical Load due to design wind speed specified in this document. The assembly should be tightened to a minimum torque as per the manufacturer installation manual. Suitable size of the bolts shall be used to avoid any future damage to the modules.
3 | SECTION – VII UNDER C. SPECIAL TECHNICAL CONDITIONS | Page 2,5,8,11,15 of 17 |  | Origin of Manufacture | Domestic
4 | SECTION - VII SCOPE OF WORKS & TECHNICAL SPECIFICATIONS | Page 61 of 136 | 16.10.1 | Conservator The conservator shall have air cell type constant oil preservation system to prevent oxidation and contamination of oil due to contact with moisture. The conservator shall be provided with separate compartment for OLTC. No separate conservator tank shall be provided for OLTC. The conservator shall be fitted with oil filling hole, cap and drain valve. Prismatic toughened glass oil level gauge and 150 mm Magnetic Oil Gauge (MOG) with low oil level alarm contact shall also be provided. | Conservator The conservator shall have air cell type constant oil preservation system to prevent oxidation and contamination of oil due to contact with moisture. The conservator shall be provided with separate compartment for OLTC. The conservator shall be fitted with oil filling hole, cap and drain valve. Prismatic toughened glass oil level gauge and 150 mm Magnetic Oil Gauge (MOG) with low oil level alarm contact shall also be provided.
5 | SECTION - VII SCOPE OF WORKS & TECHNICAL SPECIFICATIONS | Page 9 of 137 | 1.2 | Temp. coefficient of Power : Not less than -0.40% / Deg. C for crystalline Silicon | Temp. coefficient of Power : Not less than -0.43% / Deg. C for crystalline Silicon
6 | ANNEXURE TO BDS_QR | Page 5 of 6 | 1.4.1 | There can be a maximum of 03 (Three) partners in a JV/Consortium. The Lead partner of the JV/Consortium shall meet individually not less than 50% of minimum Financial Eligibility Conditions (MAAT & Working Capital) given at para 1.3 above. However, all the JV/Consortium partners must meet collectively 100% Financial Eligibility Conditions given at para 1.3 above, wherein a minimum of 20% Financial eligibility should be met individually by all other partners of the JV/Consortium. | There can be a maximum of 03 (Three) partners in a JV/Consortium. The Lead partner of the JV/Consortium shall meet individually not less than 50% of minimum Financial Eligibility Conditions (MAAT & Working Capital) given at para 1.3 above. However, all the JV/Consortium partners must meet collectively 100% Financial Eligibility Conditions given at para 1.3 above.
7 | SECTION - V SPECIAL CONDITIONS OF CONTRACT | Page 2 of 11 | 3 | The Time for Commissioning for the cumulative capacity of 100 MW Solar PV Power Plant at 05 different sites along with other associated equipment as per this tender document in total shall be 09 (Nine) Months from the Date of the Notification of Award NOA/LOA/LOI Further Contractor is also to provide Operation & Maintenance Contract of the Solar Photo Voltaic Plant for a period of 10 (Ten) years from the date of Operational Acceptance of the Plant. | The Time for Commissioning for the cumulative capacity of 100 MW Solar PV Power Plant at 05 different sites along with other associated equipment as per this tender document in total shall be 12 (Twelve) Months from the Date of the Notification of Award NOA/LOA/LOI. Further Contractor is also to provide Operation & Maintenance Contract of the Solar Photo Voltaic Plant for a period of 10 (Ten) years from the date of Operational Acceptance of the Plant. Table No 3.1 will be read out accordingly.
8 | SECTION - V SPECIAL CONDITIONS OF CONTRACT | Page 4 of 11 | 5 | 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 10% of the Contract Value (i.e., total sum of the Supply, Service and absolute value of O & M Contract). This Performance security will be valid for a total period of 72 Months (09 Months Project commissioning period + first half of the prescribed O & M Period, i.e. 60 Months + 03 Months additional) from the date of its issuance. | 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 10% of the Contract Value (i.e., total sum of the Supply, Service and absolute value of O & M Contract). This Performance security will be valid for a total period of 75 Months (12 Months Project commissioning period + first half of the prescribed O & M Period, i.e. 60 Months + 03 Months additional) from the date of its issuance. Rest of the Performance Security Clause remains the same.
9 | SECTION-VIII FORMAT FOR SOR | SOR-1 | SOR-1 | Spare Modules (As Mandatory Spares, 0.25% of total supply of solar modules) | Spare Modules (As Mandatory Spares, 0.50% of total supply of solar modules)
10 | General | - | - | Tender for Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 100 MW (AC) Solar PV Power Plant under different packages including 10 years plant O&M at Singareni Collieries Company Limited, Telangana, India | The total cumulative Project capacity has been revised to 90 MW (AC). Accordingly, the Project will be now determined as "Tender for Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 90 MW (AC) Solar PV Power Plant under different packages including 10 years plant O&M at Singareni Collieries Company Limited, Telangana, India" This revised cumulative capacity of 90 MW (AC) will supersede any other cumulative capacity mentioned anywhere in the tender document. The revised bifurcation of site capacities is mentioned in the subsequent Amendment below.
11 | General | - | - | - | Total Revised cumulative capacity = 90 MW (AC) Total No of Sites = 4 (Four) Nos including Bhupalapally Area, Mandamarri Area STG 1 , Mandamarri Area STG 2 (KASIPET MINE AREA), Kothagudam Area Bidders are required to consider the revised cumulative capacity and revised No of sites only while bidding, which is also mentioned in the table below. This revised cumulative capacity of 90 MW (AC) & revised 04 sites will supersede any other cumulative capacity and total No of sites mentioned anywhere in the tender document. Bidders are required to bid accordingly.
12 | IFB | - | -

## Clarifications
NIT No: SECI/C&P/NIT/2018/SCCL100
Tender for Design, Engineering, Supply, Construction, Erection, Testing & Commissioning of 90 MW (AC) Solar PV Power Plant under different packages including 10 years plant O&M at Singareni Collieries Company Limited, Telangana, India
Sl. No. | Tender Section | Page No. | Clause No | Description as per Tender Document | Queries | Category (Finance/Technical/Contractual) | Clarifications
1 | SECTION - V SPECIAL CONDITIONS OF CONTRACT (SCC) | 145 | 3.1 | 3.1: Commissioning of the Plant as stated under this Tender Document: D + 9 Months | Requesting SECI to Kindly reconsider the Commissioning time period for plant. As the offered site for total 100 MW and is divided into 5 Parcels with individual transmission line for each parcel. Issues such as ROW, other clearances and approvals will take time to complete. We request SECI to Consider our request and amend the completion period to at least 15 months for successful completion of project. Kindly Confirm. | Contractual | Please refer S. No. 7 of Amendment 1
2 | SECTION - V SPECIAL CONDITIONS OF CONTRACT (SCC) | 147 | 5 | Contract Performance Security | Requesting SECI to amend the contract performance security clause: As per Gazette notification dated 23/03/2012 for Public Procurement Policy notified by Government of India. Those who registered in Ministry of Micro, Small and Medium Enterprises, MSME's under NSIC are exempted for EMD, Document fee etc. Since Our Company is registered with MSME as well as with NSIC, we would like avail benefits of MSME and We request SECI to exempt the MSME from paying Contract Performance Security and allow us to participate in Upcoming opportunity. Kindly Confirm. | Contractual | The terms & conditions of the Tender document will prevail. Gazette notification dated 23/03/2012 for Public Procurement Policy notified by Government of India exempts the MSME registered entities from EMD, Document fee, however, the Performance Securities are to be paid.
3 | SECTION - V SPECIAL CONDITIONS OF CONTRACT (SCC) | 153 | 9 | 9.(C) C. For the Second Contract (related to Operation & Maintenance Part) | Please clarify that the Billing of O&M cost that It will be on Final Value quoted (including GST) in SOR II or on value which we get after applying NPV factor. Kindly Confirm. | Contractual | O&M order will be placed on the absolute value of the O&M charges & not on NPV and accordingly, the billing will be done. NPV value of O&M is the basis for the tender evaluation only.
4 | SECTION - VII A. Scope of Work | 157 | 1.2 | Origin of Manufacturer: Cells and Modules to be manufactured in India | Please clarify regarding the modules we need to consider for project, as tender specifies Domestic Category in Scope of work but in Special Technical Conditions. Its mentioned that origin of manufacturer is OPEN. Kindly Confirm which category need to be considered for this tender: OPEN or DOMESTIC? | Technical | Cells and Modules shall be domestically manufactured. Please refer S. No.3 of Amendment 1
5 | SECTION - VII A. SCOPE OF WORKS | 158 | 1 | 1. Project Particulars: CUF = 20% | Please clarify regarding the CUF that Contractor requires to maintain 20% CUF at the end of O&M Period or 20% CUF required to show in test at the end of First Year. We request SECI to kindly consider the CUF for first Year as it is difficult to Predict and commit the CUF for 10 Years period due to weather conditions, irradiation levels and other issues affecting generation. Kindly Confirm. | Technical | The CUF shall be maintained as 20% at the end of O&M Period. Please refer to the formula for calculation of CUF specified in Annexure D: PG Test Procedure, Clause 2.2 which takes into consideration PV Module degradation and Radiation.
6 | SECTION – VII C. SPECIAL TECHNICAL CONDITIONS | 312 |  | Package 3, 4 and 5 : Mandamarri-stage 1 (28MW), Mandamarri-stage 2 (15MW), Kothagudem (37MW) | As in all three packages 3,4 & 5, land offered is in different parcels/parts. I request you to please provide the distance between land parcel for better estimation of transmission line. | Technical | Please refer tentative Site Layout uploaded with the Amendments.
7 | SECTION – VII C. SPECIAL TECHNICAL CONDITIONS | 312 |  | Package 3, 4 and 5 : Mandamarri-stage 1 (28MW), Mandamarri-stage 2 (15MW), Kothagudem (37MW) | Please clarify regarding the pooling of power in Package 3, 4 & 5 that Contractor needs to pool power in specific land parcel only from another land parcel or any parcel can be used for setting up evacuation point from Solar Power Plant | Technical | Any parcel can be used for setting up evacuation point from Solar Power Plant up to the nearest Evacuation substation specified as per design unless specified otherwise in the Special Technical Specifications.
8 | SECTION – VII C. SPECIAL TECHNICAL CONDITIONS | 319 | Package 5: 4 | Package 5: Kothagudem (37MW): 4. Power Evacuation: | Single Circuit line to be considered as per Clause 4 of Package 5. Please clarify regarding the other Packages 1,2,3 &4 also that we need to consider single Circuit line or double circuit line. | Technical | Single Circuit Line shall be considered for al Packages.
9 |  |  |  | SLD | We request SECI to provide any tentative / Final SLD for all Packages / Sites. | Technical | The engineering and design of the evacuation Scheme is I the scope of the Bidder.
10 |  |  |  | General | Please Provide Drawing File / CAD file of Sites for better clarity of area | Technical | Please refer tentative Site Layout uploaded with the Amendments.
11 |  |  |  | Land and other Charges | Please confirm regarding any charges applicable for land or any fee which bidder need to be consider in their scope. | Technical | Land belongs to SCCL and hence no charges for land.
12 |  |  |  | Right of Way and other approvals. | Right Of way (ROW): Please clarify regarding the Right of way for Transmission line from Plant to S/s and transmission line to connect land parcel of one plant. I request Owner to consider ROW in their own scope or to provide necessary support to contractor. | Technical | SCCL shall provide necessary facilitation for obtaining RoW. However, the same is in the scope of the Contractor.
13 |  | 215 | 1.3.1 | The glass used to make PV modules shall be toughened low iron glass with transmittance above 90%. The minimum thickness of mono or multi crystalline modules shall be 4.0 mm for 72 cell module and 3.2 mm for 60 cell module. In case of glass-glass Modules, glass thickness on each side shall be minimum of 2 mm. | The proposed modules are already complying with IEC standards as required in the tender. Incorporating the additional requirement of thickness of 4.0 mm for 72 cell will make the project cost higher, further, such requirement of thickness is a non standard requirements. Hence, We request WBREDA to accept thickness of 3.2 mm also for 72 as a standard practice followed by SECI-THDCIL, WBSEDCL, WBPDCL, NTPC , Etc | Technical | Tender terms and conditions prevail.
14 |  | 291 | 291 | 4 nos of pyranometer and 6 nos of temperature sensor | Pls confirm is these are required on per site basis or for total 150 MW Project. | Technical | Please refer S. No. 1 of Amendment 1
15 |  | 267 | 5.1 | The Finished Grade Level (FGL) of the proposed plant shall be fixed with reference to the highest flood level (HFL) | We request SECl/SCCL to support us by providing HFL details. | Technical | It shall be the responsibility fothe bidder to ascertain
16 |  | 100 | 6.1.1, 32.1.3 | All statutory approvals/permissions and/or No Objection Certificates (No) etc. from the DISCOM for obtaining connectivity at the substation as per Project Particulars provided above. 32.1.4 In the matter of connectivity of Plant to DISCOM’s substation, the Owner will take the necessary connectivity permission. | The is contradiction in two clauses, we infer that SCCL will take grid connectivity permission.pls confirm. | Technical | SCCL will take the responsibility of grid connectivity approvals. But remaining statutory approvals if any have to be obtained by contractor.
17 |  | 268 | 5.5 | Arranging land Lease | We infer that the land is under the ownership of SCCL and will be provided along with Notice to proceed. | Technical | The land belongs to SCCL.
18 |  | 162 | 5.1.13 | 5.1.14 Laying of underground / over ground Cables (all types, as applicable) with proper arrangements along with appropriate sized ferrules, lugs, glands and terminal blocks. Laying of cables inside the building trench and other locations as required shall be over GI cable trays with proper support and accessories. | Cable tray may not be required for UG cables. | Technical | Tender terms and conditions prevail.
19 |  |  |  | Auto cad of plots | Pls support by providing autocad layout of the plots along with boundary line co-ordinates for each plot. | Technical | Please refer tentative Site Layout uploaded with the Amendments.
20 |  | 150 | 9 | E-RA on individual Site basis | Since , the package is different we request SCCL to award indivial sites to the bidders as selected through individual RA or to conduct RA for complete 150 MW Project. | Contractual | The terms & conditions of the Tender document will prevail.
21 |  | 175 | 2.1 | The work execution planning for supply, erection, commissioning and all other allied works for SPV Power Plant shall be such that it is completed within stipulated time from the date of order/ LOI/ NTP. | Project should be completed within stipulated time from the date of order/ LOI/ NTP whichever is later., pls accept as the project site is divided on several parts. | Contractual | The terms & conditions of the Tender document will prevail.
22 |  | 84 | 5.1 | At the option of the Employer/ Owner, the work for which the Tender had been invited, may be awarded to one Contractor or split between more than one bidders, in which case the award will be made for only that part of the work, in respect of which the bid has been accepted. | Since the project is in different packages , we request SCCL/SECI to to award bidders as per the selection done individually during RA. Or to confirm if all the projects will be awarded to single bidder. | Contractual | The terms & conditions of the Tender document will prevail.
23 |  | 100 | 32.1.3 | Further, contractor shall also facilitate owner in getting the required permissions/agreements as required for the energy accounting by State agencies/DISCOM. Bidders are advised to include any such costs in their final offer/Price BID. | We infer that that this project will be set up for captive Purpose. Kinley clarify what approvals are required to be taken by the contractor. | Technical | All necessary approvals required for setting up of the Plant as specified by the State and Central Regulators shall be assessed and taken by the Contractor.
24 |  | 100 | 32.1.3 | ROW | We request SCCL to take the scope of ROW in their scope or remove the scope of transmission line from bidders scope as EPC + transmission line including row may not be executed in 9 months | Technical | SCULL shall provide necessary facilitation for obtaining Row. However, the same is in the scope of the Contractor.
25 |  | 147 | 4 | However, where value of BG is Rs.5 lakhs and above, the BG should be obtained from the bank branches situated at Hyderabad / Kothagudem or operative and payable at bank branches situated at Hyderabad/ Kothagudem. | This may not be possible for the contractor to get the BG issue from Branches of Hyderabad only, we request SCCL to accept BG from banks as mentioned in the tender from any branches. | Contractual | The successful bidder has to submit PBG as per SCC clause No.5 (page 4 of 11) only.
26 |  | 415 | 14 | O & M Charges on YoY basis must be in equal or in ascending order only. | O&M Charges my differ on YoY, pls allow bidders to assume O&M value as per their discretion. | Contractual | The terms & conditions of the Tender document will prevail.
27 |  | 179 | 1.4.3 | The above warranties shall be backed by third party insurance. | Non of the Indian Module manufacturer has third party insurance , Hence, we request SECI/ SCCL to delete this clause. | Contractual | The terms & conditions of the Tender document will prevail.
28 |  | 119 | 69.1 | Action and Compensation in case of Poor/Non-compliant Work | This clause leads to interpretation of unauthentic penalty/compensation. The EIC should not be empowered with willingness to charge this compensation just by appreance of the work, hence, this may lead to contractual dispute, we request SCCL to delete this clause. | Contractual | The terms & conditions of the Tender document will prevail.
29 |  | 267 | 5.3 | cutting of trees | We infer that the land is under the ownership of SCCL, hence, land should be provided after Cutting and felling of tress to the contractor for smooth execution of the project. | Technical | Tender terms and conditions of the tender Document prevail.
30 |  | 267 | 5.3 | Approval for tree cutting | We infer that the land is under the ownership of SCCL, hence, approval for cutting of trees should be given by SCCL. | Technical | Tender terms and conditions of the tender Document prevail.
32 |  | 308 | 5.4 | As per tender document the peripheral wall will be constructed by SCCL and shall be taken out from the scope of the Contractor. | In the technical Specification boundary wall is in the scope of the contractor. Kindly confirm if the peripheral boundary wall is to be constructed by contractor or not. Further, if the peripheral boundary wall is required to be constructed by contractor then pls confirm the type of boundary required whether it will PR masonry/Chain link fencing/Pre-cast RCC | Technical | Construction of peripheral walls is in the scope of SCCL. The same is specified in the Special Technical Specifications, which prevails.
33 |  |  |  | Revised clarification after site visit | We are in the process of doing site visit, we request SECI/SCCL to allow to allow to submit revised clarification after site visit. | Contractual | Kindly refer the clarifications sheet which covers almost all categories of queries.
34 | Section-VII | 217 / 418 | 15.1.3 (viii) | Transfer of plant data reliably, to an Owner designated server | This Owner designated server is same as specified in 15.2.7 at SCCL HQ in Hyderabad?? | Technical | Yes, the owner designated server is at Hyderabad
35 | Section-VII | 218 / 418 | 15.2.1 | The SCADA System shall be built over Industrial IoT architecture with integrated Analytics, secure web access, enterprise software and Database. | SECI may pl provide list of IIOT based SCADA software vendors for our reference who will meet requirements as specified in the tender document. | Technical | No such list is available with SECI.
36 | Section-VII | 218 / 418 | 15.2.7 | A server running SCADA & Monitoring Software shall be configured in parallel with Plant Server to enable easy access to plant data from outside the plant without having to login to plant server. Effectively, the plant data shall be replicated in both places i.e. between systems at the Plant Server and Remote Server to provide data redundancy for critical plant data. | The remote server here is same as Owner designated server in various clauses 15.1.3, 15.2.7 and 15.2.9?? Plant data is getting replicated in the Owner designated server also to provide data redundancy for critical plant data. In order to have clarity on requirements, block architecture diagram to be provided. | Technical | Please refer to the Specifications for details.
37 | Section-VII | 219 / 418 | 15.3.4 | Provide web-based interface to configure the controller for various equipment in the field. | Web based interface for controller programming are not recommended because there are chances of controller memory corruption by unauthorized access. During commissioning of plant, all required data will be configured in the controllers, hence there is no need to change any configuration of controller. If case any change is required, O&M staff will do needful. | Technical | Tender terms and conditions of the tender Document prevail.
38 | Section-VII | 219 / 418 | 15.3.9 | Shall not require a static public IP address, at the plant for the purpose of remote access. | With dynamic IP, how remote access will be possible? | Technical | Dynamic DNS services enable remote access to networks with dynamic IP.
39 | Section-VII | 221 / 418 | 15.5.1 | Connectivity shall be provided to Owner’s Data Monitoring Centre.. | Where is this Owner's Data Monitoring Center located?? | Technical | Hyderabad
40 | Section-VII | 223 / 418 | 15.10.2 | Accessories :Intelligent UPS (on line): Minimum 2 hour battery backup. | Plant server and OWS will be fed from Main Control Room UPS. Separate UPS is not recommended. | Technical | Common UPS shall be acceptable.
41 | Section-VII | 223 / 418 | 15.10.2 | Operating System | Plant server will have operating system and database compatible to the SCADA software being proposed for plant, because softwares performances are linked with specific Server PC models, operating system and databases. | Technical | Tender terms and conditions of the tender Document prevail.
42 | Section-VII | 362/418 | 2.2 | Grid outage hours shall be subtracted from total number of hours in a year. The Contractor shall submit grid outage certification from competent authority of STU/DISCOM. | STU/DISCOM certification for grid loss hours may be practically difficult. Please amend the clause to competent authority of STU/DISCOM/SCCL/SECI. | Technical | Tender terms and conditions of the tender Document prevail.
43 | Section-VII | General |  | Plant layout | Please share the Auto CAD of the proposed land for understanding the area available, contour etc., | Technical | Please refer tentative Site Layout uploaded with the Amendments.
44 | Section-IV | 100/418 | 32.1.3 | In the matter of connectivity of Plant to DISCOM’s substation, the Owner will take the necessary connectivity permission, however, all the other permissions and clearances as deemed required by the State Agency/DISCOM for Bay allocation, technical/regulatory compliance for interconnection, ROW etc are to be taken by the Contractor. | Kindly inform if there are any ROW issues for laying of Tx line. Bidder may please be facilitated to carry out only works related to solar PV plant and ROW issues if any shall be resolved by M/s. SECI/SCCL | Technical | SCCL shall provide necessary facilitation for obtaining RoW. However, the same is in the scope of the Contractor.
45 | Section-VII | 176/418 | B 1.1 | Certification as per IEC, and PV Modules used in the grid connected solar power projects shall be registered with BIS and bear the Standard Mark as notified by the Bureau of Indian Standards. | BIS registration & Standard Mark on module as notified by the Bureau of Indian Standards are being done only if Solar PV module are tested as per IS standards (like IS 14286, IS/IEC 61730-1 & 2) not for the test done as per IEC standard mentioned in this clause. There are contradiction within the certification requirement & BIS marking in Module. We will provide certification as per latest IEC standard instead of BIS registration (as per IS standard) and BIS marking. Hoverer if customer require BIS registration (as per IS standard) and BIS marking can be given instead of IEC certificates. Kindly Clarify | Technical | Tender terms and conditions of the tender Document prevail.
46 | Section-VII | 180/418 | B 1.6.6 | Current binning of modules shall be employed so that current mismatch of modules in a pallet does not exceed 0.1 A. Different color codes shall be provided on the modules as well as pallet for identification of different bins. Maximum three nos. of bins will be allowed for each Module rating. | BHEL does binning as per each five wattages band by our automated packing machine instead of current binning. The same is followed for all our executed projects. Kindly accept. | Technical | Tender terms and conditions of the tender Document prevail.
47 | Section-VII-Annexure A | 326/418 | 7 | Visual test - General inspection level I | SPV module to be checked visually sampling as per Special Inspection Level S-4 and AQL 4.0% as per IS 2500 Part 1. Kindly accept. | Technical | Tender terms and conditions of the tender Document prevail.
48 | Section-VII-Annexure A | 326/418 | 7 | Flash test - General inspection level I | Performance (Flash test) of SPV module at STC sampling as per Special Inspection Level S-4 and AQL 4.0% as per IS 2500 Part 1.Kindly accept. | Technical | Tender terms and conditions of the tender Document prevail.
49 | Section-VII-Annexure A | 326/418 | 7 | EL - General inspection level I | EL test sampling as per Special Inspection Level S-4 and AQL 4.0% as per IS 2500 Part 1. Kindly accept. | Technical | Tender terms and conditions of the tender Document prevail.
50 | Section-VII | General |  | Soil resistivity | Please provide the soil resistivity to be considered by bidder for tender estimate purpose. | Technical | The data sought is not available with SECI.
51 | Section-VII | General |  | Bore well with pump | Please furnish the level of underground ground water from NGL for installation of Bore Well. Please furnish scheme or P&Ids. Further, taking permission of digging borewell in the SPV area shall lies with owner. Kindly confirm. | Technical | The data sought is not available with SECI.
52 | Section-VII | 255/418 | 22 | No. of Cameras | As per the referred clause, Number of cameras will be finalized by customer during execution of the project. However, Bidders proposal is that , in case during execution, customer requirement exceeds the bidders estimated BOQ then in such case unit rate shall be applicable. kindly confirm. | Technical | Tender terms and conditions of the tender Document prevail.
53 | Section-VII | General |  | Type test charges | Valid type test certificates (less than 10 years old) shall be submitted during detailed engineering stage. Type test shall be conducted only if valid type test certificates are not available. Type test charges are not accounted at this stage, same shall be charged to customer during execution time if type test shall be required for any supplied equipment. This is inline with the type test requirements of equipment's indicated in bid specification. Customer may please confirm. | Technical | Type test charges, if required, shall be in the scope of the Contractor and shall not be borne by SCCL.
54 | Section-VII | General |  | Topography Report & Contour map | Please furnish the topographical survey and contour map of the area to estimate the site levelling works and natural slope for drain works. | Technical | Topographical survey and contour map of the area are not available with SECI.
55 | Section-VII | General |  | Soil Investigation report | Please furnish Soil Investigation report. | Technical | Soil Investigation Report is not available with SECI
56 | Section-VII | 260/418 | 25.3 | The ROW for the TL/UG cable shall be obtained prior to the construction of the line from the concerned authorities | Please clarify scope. Is there any private land through which the evacuation line has to be constructed? | Technical | Yes, There are some private lands.
57 | Section-VII | 283/418 | 13.25 | Modules shall be clamped & bolted with the structure properly. The material of clamps shall be Al / SS – 316 having weather resistant properties. Clamp/bolt shall use EPDM rubber and shall be designed in such a way so as not to cast any shadow on the active part of a module | Please specify if the PV-Modules have to be Clamped and Bolted both to the structure?? Also use of EPDM may be waived off as it may not last for 25 years in outdoor condition. | Technical | Please refer S. No. 2 of Amendment 1
58 | Section-VII | 281/418 | 13.07 | The minimum thickness excluding anti corrosive treatment (BMT) of various elements of MMS structure shall be as following: • Stub/ column – 3.15mm, Rafter – 2.5mm & • Purlin & other members – 2.0mm | The thickness of MMS members to be arrived as per design calculations. Suggested thickness-( Column -2.5mm,Rafter -2.0mm and Purlin-1.6mm) | Technical | Tender terms and conditions of the tender Document prevail.
59 | Section-VII | 283/418 | 13.23 | Fasteners and washers to be used for erection of mounting structures and those for fixing Module over MMS shall be of stainless steel grade SS 304 & SS 316 with property class A-70 conforming to relevant ISO standard and must sustain the adverse climatic conditions to ensure the life of the structure for 25 years. | Please specify the grade of stainless steel fasteners for Mounting Structure has to be SS304 and for PV Module fastening has to be SS316. For the above case grade of SS304 has to be A2 and SS316 has to be A4 . Please confirm. | Technical | Tender terms and conditions of the tender Document prevail.
60 |  | General |  | General | We request that Anti Dumping Duty, Safeguard Duty shall be borne by SCCL. Kindly Accept. | Contractual | The terms &
61 |  | General |  | General | If delay from scheduled completion is on account of employer, then any statutory variation beyond stipulated Delivery/ Commissioning/Completion schedule shall be to customer’s account. | Contractual | The terms & conditions of the Tender document will prevail.
62 |  | General |  | General | Applicable taxes & duties on contract cancellation charges shall be on account of employer. | Contractual | The terms & conditions of the Tender document will prevail.
63 | Section-V | 150/418 | 9 | Interest bearing adjustable initial advance (OPTIONAL) of 10% of the Contract Value (i.e., total sum of all the Supply Contract) shall be released to successful bidder upon receipt of unconditional acceptance of NOA | We request to give interest free advance. Kindly accept. We request to submit unconditional Bank Guarantee for 100% of advance amount. Kindly accept. | Contractual | The terms & conditions of the Tender document will prevail.
64 | Section-VII | 179/418 | 1.4.3 | Warranty: The above warranties shall be backed by third party insurance. | We kindly request you to also accept the provision of providing Bank Guarantee also for the solar PV modules warranty as accepted in all other tenders. | Contractual | The terms & conditions of the Tender document will prevail.
65 | Section-VII | 177/418 | 1.3.1 | For PV Modules with backsheet, toughened low iron glass with minimum thickness of 4.0 mm for 72 cell module and 3.2 mm for 60 cell module for multi or mono-crystalline modules. | Kindly amend the clause as follows: The glass used to make PV Modules shall be toughened low iron glass with minimum thickness of 3.2 mm as module manufacturer with 4.0 mm glass are very few thereby limiting the bidders to approach those manufacturer only. | Technical | Tender terms and conditions of the tender Document prevail.
66 | Section-V (SCC) | 145/418 | 3 | The Time for Commissioning for the cumulative capacity of 100 MW Solar PV Power Plant at 05 different sites along with other associated equipment as per this tender document in total shall be 09 (Nine) Months from the Date of the Notification of Award NOA/LOA/LOI | We Kindly request you to increase the time of commissioning to 12 months from NOA | Contractual | Please refer S. No. 7 of Amendment 1
67 | Section-IIII (BDS) | 63/418 | 13 | State of which stamp paper is required for Contract Agreement: Telangana | We kindly request you to keep the choice open for using stamp paper from any state for contract agreement. Please accept | Contractual | The terms & conditions of the Tender document will prevail.
68 | Section-V (SCC) | 145/418 | 3 | Issue of NOA as zero date | We kindly request you to accept that zero date or effective date should be the date of handover of complete encumbrance free land to the successful bidder not the issue of NOA | Contractual | The land is already completely encumbrance free, which is under the possession of SCCL
69 | Section-VII | 266/418 | 3.1 | All buildings/ Open installations (MCR, LCR etc.), Switchyard and Sub-station area shall have levelled ground. No foundation for MMS, Buildings, Switch yard equipment & structures, Sub-stations, HT Line Towers, Transformer etc. shall rest on filled up ground. However, minor structures like cable trench, cable rack, pipe pedestal etc. may rest in filled up soil with max. safe bearing capacity for design consideration not more than 3 T/m2. | Foundation over the filled up soil of 95% consolidation may be allowed. | Technical | Tender terms and conditions of the tender Document prevail.
70 | Section-VII | 267/418 | 5.3 | The contractor is responsible for making the site ready and easily approachable by clearing bushes, felling of trees (mandatory permissions/ licenses/ statutory clearances from competent authorities if required for cutting of trees, blasting or mining operations, disposal of waste material etc. shall be obtained by the contractor), cutting, filling with selected excavated earth or borrowed earth including identifying borrow areas | Contractor will cut the tree after the land owner obtains the permission from Forest dept. Please confirm | Technical | It is the responsibility of the contractor for obtaining approvals from forest department. However SCCL will facilitate for obtaing the same.
71 | Section-VII | 183/418 | 4 | Power Conditioning Unit | Kindly confirm whether string inverter/ Containerized PCU/Outdoor Inverter is acceptable | Technical | Outdoor PCU is acceptable as per the Technical specifications provided.
72 | Section-VII | 285/418 | 16.1.2 | Unless otherwise specified elsewhere, all buildings except Security room/ cabin shall have RCC framed structure. Brick partition walls shall be provided for Kitchen, Pantry, Battery room and Toilet units. For other rooms AL Glass partitions shall be provided. The equipment area shall be designed with OEM requirements to ensure all satisfactory operations. The security room/ cabin(s) shall be of prefabricated structure. | PEB control room and PEB LCR(inverter room) may be allowed to expedite the work as RCC buildings take a lot time and considering the completion time, it is feasible to allowed PEB inverter and control room. Same is accepted in other tenders also. | Technical | Tender terms and conditions of the tender Document prevail.
73 | Section-VII | 293/418 | 30.2 | Wall and ceiling plaster shall be in cement mortar (CM) 1:6 and 1:3 respectively | Ceiling plaster may not be required if we use fair face ply shuttering. Ceiling plaster will be provided if using steel plate shuttering. Pl. confirm. | Technical - Civil | Tender terms and conditions of the tender Document prevail.
74 | Section-VII | 293/418 | 32.1 | The Contractor shall design & provide soak pit and RCC Septic tank for treatment of sewage and waste water from MCR/LCR building and Security room. The septic shall be designed as liquid retaining structure conforming to IS:3370 for design loads as specified under Clause No.10. | Septic tank will be constructed with brick work as per IS 2470. Pl. review. | Technical - Civil | Tender terms and conditions of the tender Document prevail.
75 | Section-VII | General |  | Layout | Fencing & peripheral road around occupied land & encroachment land is not the part of EPC scope.Pl. confirm | Technical | Construction of peripheral walls is in the scope of SCCL. The same is specified in the Special Technical Specifications, which prevails.
76 |  | General |  | Price BID | The rate of Safe-Guard Duty is not fixed and varies with time. SECI may indicate the month in which the LOA shall be placed enable Bidder mention exact rate of Safe-Guard Duty applicable in the Bid. Alternately, SECI to specify the % SGD to be considered in the Bid and the value of the Module price for bringing parity among bidders and then adjust the Bid Price with actual rate of SGD applicable after 1/3rd time of LOA to arrive at the Contract Price at the time of releasing LOA. | Contractual | The terms & conditions of the Tender document will prevail.
77 |  | General |  | Customs duty on SPV modules |  | Contractual | Bidders are required to exercise their own due diligence & discretion while deciding on the matters of Safe Guard Duty.
78 |  | General |  | Payment to MSMEs | Purchaser to make registration of Bidders on the Trade Receivables Discounting System (TReDS) platform (www.rxil.in) compulsory for all Bidders to bring parity among bidders and ensure adherence to Govt Policies. | Contractual | SECI is already on board with TReDS
79 |  | General |  | Techno Commercial Bid Opening | In line with Guidelines of transparent bid opening procedure participation in techno-commercial Bid opening may be made OPTIONAL to be Bidders. | Contractual | Bidders can join individually for the offline Bid opening event wherein the Offline documents like EMD, Bid Processing Fee, Pass Phrase, BR etc is checked at the due time & date of offline Bid opening event. However, Its an online tender wherein the all other Techno commercial & Financial bid opening events are executed online & it can be simultaneously seen by all of the qualified bidders on real time basis from their respective TCIL Login. So, the Physical presence in this case is not required.
80 |  | General |  | Price Bid Opening | In line with Guidelines of transparent bid opening procedure participation in techno-commercial Bid opening may be made OPTIONAL to be Bidders. | Contractual | Bidders can join individually for the offline Bid opening event wherein the Offline documents like EMD, Bid Processing Fee, Pass Phrase, BR etc is checked at the due time & date of offline Bid opening event. However, Its an online tender wherein the all other Techno commercial & Financial bid opening events are executed online & it can be simultaneously seen by all of the qualified bidders on real time basis from their respective TCIL Login. So, the Physical presence in this case is not required.
81 |  | General |  | Bank Guarantee | The Bank Guarantee shall be issued by the Bank in the city from where the BG is issued and any notice of its appropriation shall be valid if the notice reaches the Bank within the specified date. Hence, any action on the Bank Guarantee is valid only if it happens in the city from which the Bank Guarantee is issued. Hence, applicability of stamp duty at SECI (Employer address) or SECI Site is not applicable. However, if SECI desires that the notice of appropriation shall be issued by SECI HQ / SECI Site to the nearest branch of the bank, SECI to inform the city / district where the BG notice should be applicable so that necessary arrangement in the BG shall be made. The specific clause that will be required to be inserted in the BG for making such a notice valid, will be taken up with the bank and informed to Employer to take necessary decision regarding amendment of the ITB once the clarification to above is received. | Contractual | Tender terms and conditions of the tender Document prevail.
82 | Section-VII | 203/418 | 7.8.2 | LT cable (from inverter to inverter transformer) shall laid through RCC cable trench with supports. | We kindly request you to accept PCC trench instead of RCC as this will consume a lot of time and with time line of just 9 months, it is feasible to allow PCC trench as same is allowed in other tenders. | Technical
83 | Section-V | 147/418 | 5 | CPBG submission | We kindly request to allow the bidder to submit CPBG within 30 days from the date of handing over of encumbrance free land to successful bidder instead of issuing of NOA | Contractual | Kindly refer the Point No 68 above.
84 | Section-V | 147/418 | 5 | First Stage (Supply and Services): The value of the Contract Performance Security shall be 10% of the Contract Value and will remain valid 72 months from date of issuance Second Stage (O&M): The Performance security shall be furnished 30 days prior to completion of first 05 years of O&M and value of the Contract Performance Security shall be 05% of the Contract Value | We kindly request you to accept CPBG-1 of 5% of contract value excluding O&M charges with validity up to Defect liability period as the O&M will be started after operational acceptance and bidder will be providing separate BG for that. We also request you to accept CPBG-II for O&M with amount of 10% of O&M value with initial validity of one year which will be extended from time to time and value will be reduced after completion of each year O&M as allowed in other tenders. | Contractual | The terms & conditions of the Tender document will prevail.
85 | Section-IV | 79/418 | 1.1.30 | EFFECTIVE DATE means the date of issuance of Notification of Award from which the Time for Completion shall be determined or any other specific date as provided in the Notice to Proceed(NAP) for exceptional cases | We kindly requested you that effective date should be considered as date of handing over of complete encumbrance free land to bidder and subsequently zero date and date of completion to be changed accordingly as there have been instances where NOA has been awarded but land has been awarded at a later stage. | Contractual | Kindly refer the Point No 68 above.
86 | Section-IV | 84/418 | 5.1 | The right to accept the Tender will rest with the Employer/ Owner. The Employer/ Owner, however, does not bind himself to accept the lowest Tender, and reserves to itself the authority to reject any or all the Tenders received without assigning any reason whatsoever. At the option of the Employer/ Owner, the work for which the Tender had been invited, may be awarded to one Contractor or split between more than one bidders, | We kindly request to waive off this clause as this doesn’t guarantee that project will be awarded to the L-1 bidder. | Contractual | The terms & conditions of the Tender document will prevail.
87 | Section-IV | 91/418 | 19 | Force Majeure | We kindly request to include local disturbances and public outrage to be included in the force majeure events. | Contractual | Local disturbances and public outrage can not be included under Force Majeure clause
88 | Section-IV | 92/418 | 19.7 | If works are suspended by Force Majeure conditions lasting for more than two months, the Employer/Owner shall have the option of cancelling this Contract in whole or part thereof, at its discretion. | We kindly request you to waive off this clause. | Contractual | The terms & conditions of the Tender document will prevail.
89 | Section-IV | 96/418 | 25.3 | Termination for Convenience The Owner may, by written notice sent to the Contractor, terminate the Contract, in whole or in part, at any time for its convenience. The notice of termination shall specify that termination is for the Owner’s convenience, the extent to which performance of work under the Contract is terminated, and the date upon which such termination becomes effective. | We kindly request you to waive off this clause as reason for termination should be on some valid ground like on grounds of EPC bidder not following specifications not because of customer convenience. | Contractual | The terms & conditions of the Tender document will prevail.
90 | Section-IV | 92/418 | 20 | Liquidated damages for Delay half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages | We kindly request you to amend the clause as 0.5% per week of the Contract Price (excluding O&M) for the uncommission portion as liquidated damages. Kindly accept | Contractual | The terms & conditions of the Tender document will prevail.
91 | Section-IV | 129/418 | 81.1.4 | Owner shall make all endeavor to make payments of undisputed amount of the bills submitted based on the joint measurements within 30 (Thirty) days from the date of certification by the Engineer-in-Charge/Project Manager. | We kindly request to reduce the date of payment from within 30 days to within 15 days from the date of certification as this is short term project and payment to be made as quick as possible for more workers to rope into the project and maintaining delivery schedule. | Contractual | The terms & conditions of the Tender document will prevail.
92 | Section-IV | 133/418 | 93.3 | However, any increase in the rate of these taxes, duties and levies beyond the contractual completion period shall be to Contractor's account and any decrease shall be passed on to Owner | Kindly remove the portion where it is stated that any decrease shall be passed to owner | Contractual | The terms & conditions of the Tender document will prevail.
93 | Section-VII | 178/418 | 1.3.7 | Each PV Module shall be provided a bar code which is embedded inside the module lamination and must be able to withstand harsh environmental conditions. The bar code data base shall contain the following information. Bar code scanner and database of all the modules containing the following information shall also be provided. | We kindly request you to accept RFID tag as RFID tag includes all the details which have been desired in the specification as allowed in all other solar tenders. Each PV module deployed must use a Radio Frequency identification (RFID) tag for traceability. RFID shall either be placed behind name plate sticker or behind bar code label pasted on the back glass of PV module and must be able to withstand harsh environmental conditions during the module lifetime. One number RFID reader has to be supplied by the bidder which has to be compatible to read the data from the RFID Tag & download the data to Computer. Bar code with Sl.no. will be put inside the laminate. I-V data will be encoded in RFID Tag | Technical | Tender terms and conditions of the tender Document prevail.
94 |  | General |  | Vendor Approval for Works | Kindly inform if any vendor approval for works is required | Technical | No. However the bidder shall chose experienced sub vendors for various works involved.
95 | Section-VII | 364/418 | Annex-D | Mandatory spares- PV Modules-0.5% of total supply | These clauses are contradictory. Kindly confirm the final list of required mandatory spares. | Technical | Please refer S. No. 9 of Amendment 1
96 |  |  | SOR-1 | Spare Modules (As Mandatory Spares, 0.25% of total supply of solar modules) |  | Technical
97 | Section-VII | 176/418 | 1.1 | 1. IEC 61215-1 – Ed. 1.0 (Design Qualification and Type Approval-Part 1:Test requirement) 2. IEC 61215-1-1-Ed.1.0 (Design Qualification and Type Approval-Part 1-1:Special requirement for testing of crystalline silicon photovoltaic(PV) modules) 3. IEC 61215-1-2-Ed.1.0 0 (Design Qualification and Type Approval-Part 1-1:Special requirement for testing of thin film cadmium telluride (CdTe) based photo- voltaic (PV) modules) 4. IEC 61730-1-Ed. 2 (Safety Qualification – Part 1: Requirement of construction) 5. IEC 61730-2-Ed. 2 (Safety Qualification – Part 2 : Requirement of Testing) 6. IEC 61701-2-Ed. 2 (Salt mist corrosion testing of photovoltaic (PV) modules) | Most of the reputed Indian vendors do not have certificates with 2016 version of IEC 61215 & 61730. Request to accept present version of 2005-Edition 2 for IEC 61215 and 2004 version for IEC 61730- 1 & 2. Insisting on 2016 version will restrict the vendors and also delay in availability of PV modules. It may please be noted BIS also specified 61215:2005 version & 61730 -2004 version. Pl. accept BIS certificate as per MNRE certification | Technical | Tender terms and conditions of the tender Document prevail.
98 | Section-VII | 176/418 | 1.1 | PV Module should have been included in the ALMM List as per MNRE approved model | This is new requirement from MNRE and will be followed after implementation. Kindly accept | Technical | The said Order is said to be implemented from 1st April 2020.
99 | Section-VII | 177/418 | 1.2 | Temp. coefficient of Power : -0.40% / Deg. C or better for crystalline Silicon | Pl. accept -0.43% / Deg. C or better as this clause will restrict the vendors. | Technical | Please refer S. No. 5 of Amendment 1
100 | Section-VII | 178/418 | 1.3.7 | Bar code inside the laminate with module I-V data. | Bar code with Sl.no. will be put inside the laminate. I-V data will be encoded in RFID Tag | Technical | Tender terms and conditions of the tender Document prevail.
101 | Section-VII | General |  | Sub-Vendor List | No specific vendor list is being provided in the tender. Kindly inform whether bidder can proceed with their PMD vendors for raw material and bought out items. | Technical | Yes, bidder can proceed with their PMD vendors for raw material and bought out items.
102 | IFB | 5 | General | BIDDERS ARE REQUIRED TO QUOTE ACCORDINGLY FOR THE COMPLETE CUMULATIVE CAPACITY OF 100 MW (AC). | Kindly allow to participate in part of the 5 different project site details mentioned from SITE-1 to SITE-5. | Contractual | The terms & conditions of the Tender document will prevail.
103 | BDS | 4 of 6 | 1.3 | The Minimum Average Annual Turnover (MAAT) of the bidder in the last three financial years (i.e.FY 2015-2016, 2016-17 and 2017-18) should be INR 1,81,60,00,000/- | We request you to change this clause as follows, The Minimum Average Annual Turnover (MAAT) of the bidder in the last three financial years (i.e.FY 2015-2016, 2016-17 and 2017-18) should be INR 1,81,00,000/- per MW for applied Capacity of the bidder. | Contractual | The terms & conditions of the Tender document will prevail.
104 | BDS | 4 of 6 | 1.3 | The bidder should have a minimum Working Capital of INR 1,13,50,00,000/- (Indian Rupees One Hundred and thirteen crores & fifty lacs only) | The bidder should have a minimum Working Capital of INR 1,00,00,000/- per MW for applied capacity of the bidder | Contractual | The terms & conditions of the Tender document will prevail.
105 | ITB | 30 of 45 | 40 | PUBLIC PROCUREMENT POLICY FOR MICRO AND SMALL ENTERPRISES (MSEs) | We are registered with Udyog Aadhaar as MSE. Kindly Confirm that, you will provide all benefits for MSE registered members as per law including price preference policy | Contractual | Kindly go through the clause related to entities registered under MSME in the tender document.
106 | SCC | 2 of 11 | 3 | The Time for Commissioning for the cumulative capacity of 100 MW Solar PV Power Plant at 05 different sites along with other associated equipment as per this tender document in total shall be 09 (Nine) Months from the Date of the Notification of Award NOA/LOA/LOI | Considering present delivery schedule of various components (including module), project site location and contractor’s scope of work, we request you to consider completion period of 15 (Fifteen) Months from the date of signing of contract agreement or site handover to the contractor. | Contractual | Please refer S. No. 7 of Amendment 1
107 | SCC | 4 of 11 | 5 | Contract Performance Security | We request you to ammend this clause as follows:- 1. First Stage (Supply and Services): The value of the Contract Performance Security shall be 10% of the Contract Value (i.e., total sum of the Supply, Service Contract). This Performance security will be valid for a total period of project commissioning (i.e. Project commissioning period + 03Months additional) from the date of its issuance. 2. Second Stage (O&M): The Performance security shall be furnished 30 days prior to the completion of first stage Performance Security & it shall be equivalent to the 05% of the O&M Contract Value (i.e., total sum of the absolute value of O & M Contract). This Performance security will be valid for a total period of O&M contract (Total O & M Period, i.e. 120 Months + 03 Months additional) from the date of its issuance 3. Contractor needs to furnish the revised Contract Performance Security amounting to 05% (under Second Stage) of the total O&M Contract Value as mentioned above within the validity period of the Contract Performance Security submitted at First Stage. | Contractual | The terms & conditions of the Tender document will prevail.
108 | GCC | 12 of 73 | 2.3 | Construction Water Supply | We request you to provide water free supply during execution and O&M Period | Technical | It is the responsibility of the contractor.
109 | GCC | 12 of 73 | 2.4 | Construction Power Supply | We request you to provide power free supply during execution and O&M Period | Technical | It is the responsibility of the contractor.
110 | GCC | 63 of 73 | 94.1 | During the Contract period including O&M period, i.e., during Construction & O&M period, all insurance related expenses shall be borne by the Contractor. | As per norms & rules, During construction period all insurances shall be borne by bidder During O&M period all insurances shall be borne by you/Owner as per the IRDA rule | Contractual | The terms & conditions of the Tender document will prevail.
111 | General |  |  | Equipment Warranties | We shall provide Warranty/Guarantee period for all equipment’s as per the OEM’s recommendations. | Contractual | The terms & conditions of the Tender document will prevail.
112 | SECTION - III | Page 5 of 6 | 1.4.1 | There can be a maximum of 03 (Three) partners in a JV/Consortium. The Lead partner of the JV/Consortium shall meet individually not less than 50% of minimum Financial Eligibility Conditions (MAAT & Working Capital) given at para 1.3 above. However, all the JV/Consortium partners must meet collectively 100% Financial Eligibility Conditions given at para 1.3 above, wherein a minimum of 20% Financial eligibility should be met individually by all other partners of the JV/Consortium. | Please note that as per clause, lead partner has to have at least 50% Financial capabilities and all partners put together should have 100% Financial capabilities. We request that requirement for each partner to additionally qualify at least 20% Financial eligibility should be withdrawn. We recommend that all parties put together should meet 100% Financials and 100% Technical requirement without specific 20% individual financial qualification requirement. | Contractual | Please refer S. No. 6 of Amendment 1
113 | SECTION - V | Page 2 of 11 | 3 | The Time for Commissioning for the cumulative capacity of 100MW Solar PV Power Plant at 05 different sites along with other associated equipment as per this tender document in total shall be 09 (Nine) Months from the Date of the Notification of Award NOA/LOA/LOIN. | As per our assessment of all the sites, it is observed that locations are at remote locations and also need certain forest cleaning, leveling and are at scattered height locations. Some of the sites have requirement to get necessary ROW for line evacuation of power. Further 4 locations are to be developed simultaneously. Taking a comprehensive view of the above issues, it is unlikely that project could be implemented to the satisfaction of the owner / employer before 12 months from date of issue of LOA. Hence we request you to kindly increase the development time period suitably. | Technical | Please refer S. No. 7 of Amendment 1
114 | SECTION - VII | Page 3 of 14 | 1 | Origin of manufacturer :Cells and Modules to be manufactured in India | As per Technical requirements, Cell and Modules are to be sourced from manufacturers in India. Please note that the manufacturing at India, especially for Cells, is at nascent stage with very limited credible manufactures in the market. We suspect that sourcing of Cells and modules from these limited players will lead to substantial increase in Project Cost and is sub-optimal for the Owner. Hence we request you to kindly allow the sourcing from any manufacturers and not specifically from Indian manufacturers. | Technical | Tender terms and conditions of the tender Document prevail.
115 | III (annexure to Bids) | 3 of 6 | 1.2 | IIA The bidder should have experience in execution of Ground mounted Solar Projects as a Developer of Grid-connected Solar PV Power Plant(s) of cumulative Capacity not less than 50 (Fifty) MW in last seven Financial years as on last date of bid submission. However, such Grid connected Solar PV Power Plant capacity must have been in satisfactory operation for at least six (06) months prior to the last date of bid submission. | BEL has successfully commissioned 49.5 MW(Ac) ground mounted solar projects in the developers mode in the last 2 years and all of them are in satisfactory operation for more than 6 months. Can you consider this capacity as the qualifying requirements and allow BEL to Qualify in technical eligibility conditions. | Contractual | The terms & conditions of the Tender document will prevail.
116 | IV,GCC | 22 of 73 | 20.1 | Subject to Force Majeure Clause, if the Contractor fails to comply with the Time for Completion /successful commissioning of Plant facilities in accordance with SCC Clause for the whole of the facilities then the Contractor shall pay to the Owner a sum equivalent to half percent (0.5%) per week of the Contract Price for the whole of the facilities as liquidated damages for such default and not as a penalty, without prejudice to the Owner’s other remedies under the Contract subject to the maximum limit of five percent (05%) of Contract Price for the whole of the facilities. | Could you make this clause applicable only to the work that is not completed within the due date, not for the whole of the facilities? | Contractual | The terms & conditions of the Tender document will prevail.
117 | V, SCC | 2 of 11 | 3 | The Time for Commissioning for the cumulative capacity of 100 MW Solar PV Power Plant at 05 different sites along with other associated equipment as per this tender document in total shall be 09 (Nine) Months from the Date of the Notification of Award NOA/LOA/LOI | Considering the time required for various clearances and approvals, could you make the time for commissioning for all projects as 15 months from the date of the NoA/LoA/LoI | Technical | Please refer S. No. 7 of Amendment 1
118 | V, SCC | 2 of 11 | 3 | The Time for Commissioning for the cumulative capacity of 100 MW Solar PV Power Plant at 05 different sites along with other associated equipment as per this tender document in total shall be 09 (Nine) Months from the Date of the Notification of Award NOA/LOA/LOI | As the sites are different and the power evacuation is also from different Sss, We request you to allow project wise commissioning, instead as a whole for 100 MW | Technical | Tender terms and conditions of the tender Document prevail.
119 | V, SCC | 5 of 11 | 6 | During the Operational Acceptance after providing 03 chances for the PR demonstration, any shortfall in the Performance Ratio (PR) as determined through the PR Test Procedure specified in Section VII, Scope of Work and Technical Specifications, & “PERFORMANCE GUARANTEE TEST PROCEDURE”, will attract imposition of penalty. For every 0.01 shortfall in PR below the committed PR value, a penalty of 1% of the total Contract Value (i.e., total sum of all the Supply, Service and absolute value of O & M Contract) shall be levied. In case the Contract Performance Security has already been encashed on account of any default/delays, the penalty amount will be recovered from any due payments to the contractor. In case the Plant PR Shortfall is more than 0.05 than the specified PR value, then the total plant will be accepted on as-is basis & the total Contract Performance…………………. | Requested to review the quantum of penalties and reduce the same as a motivating factors | Contractual | The terms & conditions of the Tender document will prevail.
120 | VII,SoW | 4 of 14 | 1, Project Particulars | performance parameters | CUF of 20% is on the higher side and which cannot achieved with 10% loading on dc side. We request you make downward revision of CUF to a min 18.0% | Technical | Tender terms and conditions of the tender Document prevail. The bidder may chose to install higher DC capacity to meet the requirement.
121 | VII,B Technical Specs | 8 of 136 | 1.1 | IEC 62716:2013 Photovoltaic (PV) modules - Ammonia corrosion testing Ed.1 | Is IEC 62716 really required as sites are free from such environment. Request you to be done away with this requirement | Technical | Tender terms and conditions of the tender Document prevail.
122 | VII,B Technical Specs | 9 of 136 | 1.2 | Module Efficiency : ≥ 17% for Mono-crystalline | Review this requirement as there are hardly no/one manufacturer of monocrystalline cells in India meeting this specs, which may lead to increased cost. | Technical | Tender terms and conditions of the tender Document prevail.
123 | VII,B Technical Specs | 9 of 136 | 1.3.1 | The glass used to make PV modules shall be toughened low iron glass with transmittance above 90%. The minimum thickness of mono or multi crystalline modules shall be 4.0 mm for 72 cell module and 3.2 mm for 60 cell module. In case of glass-glass Modules, glass thickness on each side shall be minimum of 2 mm. It shall be laminated using a laminator with symmetrical structure, i.e. heating plates on both sides. | 3.2 mm glass for 72 cells modules have passed IEC tests. Could you consider the same for 72 cells modules? | Technical | Tender terms and conditions of the tender Document prevail. Separate IEC test not required for change in thickness of glass.
124 | VII,B Technical Specs | 10 of 136 | 1.3.7 | Each PV Module shall be provided a bar code which is embedded inside the module lamination and must be able to withstand harsh environmental conditions. The bar code data base shall contain the following information. Bar code scanner and database of all the modules containing the following information shall also be provided. | Normally, the data is embedded in back label not in the bar code. Could you consider the same ie data writing in back label. | Technical | Tender terms and conditions of the tender Document prevail.
125 | VII,B Technical Specs | 105 of 136 | 8.5 | Barbed wire fencing | During Pre-bid meeting it has been informed that the sites shall be provided with boundary wall, pls confirm. | Technical | Boundary Wall is in the Scope of Owner i.e. SCCL.
126 | VII, C Special Technical Specs | 1 of 17 |  | Land Ownership | Pls confirm whether proposed sites are in complete ownership of M/s SCCL | Technical | Yes
127 | GCC | Page 30 of 73 | 32.1.3 | Connectivity of Plant to DISCOM’s substation | Pls confirm the boundary limits for this work. All requirement for the Solar Power Plant shall be complied. Any changes in meter infrastructure of M/s SCCL shall be taken by the Owner. | Technical | Please refer tentative Site Layout uploaded with the Amendments.
128 | VII, C Special Technical Specs | 17 of 17 | 4.1 | Laying second 132 kV circuit on the existing dedicated 132 kV Single circuit transmission line | In the absence of the permission to lay the second conductor, additional charges towards erection of towers as per actuals shall be paid by the Owner. | Technical | Yes
Note on I99: Prashant: May like to consider approval of vendors to ensure quality.